## PPC_Sequences
Seq | Step | Action | Interlock_Group | Purpose | Channel | Unit ID | Function code | Register type | Register (DEC) | CNT (WORD) | Data type | Format | Scaling | Offset | Unit | Access | Value / Condition | Notes
S1 | 1 | WRITE | G1 Run/Standby | Allow inverter to operate (precondition for InvOpMod=Operation). | RemRdy | 3 | 0x03 | Holding | 2 | 2 | S32 | ENUM | 1 | 0 | - | RW | 308 (Ready) | Write RemRdy=308 before InvOpMod=308.
S1 | 2 | WRITE | G1 Run/Standby | Request inverter RUN/Operation. | InvOpMod | 3 | 0x03 | Holding | 0 | 2 | S32 | ENUM | 1 | 0 | - | RW | 308 (Operation) | Start requires RemRdy=308 AND InvOpMod=308.
S1 | 3 | WAIT/VERIFY | G4 Fault Handling | Confirm no active fault before enabling PPC modes. | ErrStt | 3 | 0x04 | Input | 94 | 2 | S32 | ENUM | 1 | 0 | - | RO | ErrStt == 0 | If ErrStt !=0, go to S3 fault handling.
S1 | 4 | WRITE | G2 Active Power Control | Select active power control via communication (PPC/SCADA). | GriMng.WMod | 3 | 0x03 | Holding | 6 | 2 | S32 | ENUM | 1 | 0 | - | RW | 1079 (WCtlCom) | Must set WMod=1079 before writing WSpt.
S1 | 5 | WRITE | G3 Reactive/PowerFactor Control | Select reactive power (Q) or PF control via communication. | GriMng.VArMod | 3 | 0x03 | Holding | 4 | 2 | S32 | ENUM | 1 | 0 | - | RW | 1072 (VArCtlCom) OR 1075 (PFCtlCom) | Choose 1072 for Q setpoint (VArSpt) or 1075 for PF setpoint (PFSpt).
S2 | 1 | WRITE | G2 Active Power Control | Per-inverter active power setpoint. | WSpt | 3 | 0x04 | Input | 108 | 2 | S32 | FIX0 | 1 | 0 | kW | RO | P_cmd_i (kW) | Per map WSpt is RO (Input @108). SMA docs treat WSpt as setpoint parameter; verify write access in your Modbus write DB / profile.
S2 | 2 | WRITE | G3 Reactive/PowerFactor Control | Per-inverter reactive power setpoint (if Q control). | VArSpt | 3 | 0x04 | Input | 112 | 2 | S32 | FIX0 | 1 | 0 | kVAr | RO | Q_cmd_i (kVAr) | Write only when VArMod=1072. Verify write access (map shows RO Input @112).
S2 | 3 | WRITE | G3 Reactive/PowerFactor Control | Per-inverter power factor setpoint (if PF control). | PFSpt | 3 | 0x04 | Input | 114 | 2 | S32 | FIX4 | 10000 | 0 | - | RO | PF_cmd (cosφ) | Write only when VArMod=1075. Verify write access (map shows RO Input @114).
S2 | 4 | READ/SUPERVISE | Operational | Supervise available active power. | WAval | 3 | 0x04 | Input | 172 | 2 | S32 | FIX4 | 10000 | 0 | pu | RO | WAval > 0 (kW) | If WAval collapses (e.g., derating), recompute distribution.
S2 | 5 | READ/SUPERVISE | Operational | Supervise available reactive power. | VArAval | 3 | 0x04 | Input | 174 | 2 | S32 | FIX4 | 10000 | 0 | pu | RO | VArAval within capability | Clamp Q/PF commands to capability and grid-code limits.
S2 | 6 | READ/SUPERVISE | Operational | Detect why inverter disconnected. | PwrOffReas | 3 | 0x04 | Input | 178 | 2 | S32 | ENUM | 1 | 0 | - | RO | PwrOffReas == 0 or not stop-by-command | Use PwrOffReas for diagnostics / inhibit auto-restart per site rules.
S2 | 7 | READ/SUPERVISE | Operational | Detect derating state. | DrtStt | 3 | 0x04 | Input | 176 | 2 | S32 | ENUM | 1 | 0 | - | RO | Derating status | Use derate factor when computing PmaxPlant.
S3 | 1 | TRIGGER | G4 Fault Handling | Fault detected. | ErrStt | 3 | 0x04 | Input | 94 | 2 | S32 | ENUM | 1 | 0 | - | RO | ErrStt != 0 | Stop dispatch to faulted inverter(s); hold P_i=0 for that unit.
S3 | 2 | READ | G4 Fault Handling | Capture error number for SCADA/utility reporting. | ErrNo | 3 | 0x04 | Input | 96 | 2 | U32 | FIX0 | 1 | 0 | - | RO | ErrNo
S3 | 3 | WRITE | G4 Fault Handling | Acknowledge present error after fault cause removed. | ErrClr | 3 | 0x03 | Holding | 8 | 2 | S32 | ENUM | 1 | 0 | - | RW | 26 (Ackn) - ONE SHOT | Do not pulse continuously; use a one-shot with lockout timer.
S3 | 4 | OPTIONAL WRITE | G4 Fault Handling | Acknowledge safety-relevant errors (procedure-based). | ErrClr.ProErr | 3 | 0x03 | Holding | 20 | 2 | S32 | ENUM | 1 | 0 | - | RW | 973 (Acknowledge ProErr) | Use only when your O&M procedure allows; typically not automatic.
S3 | 5 | WAIT/VERIFY | G4 Fault Handling | Confirm fault cleared before restart sequence S1. | ErrStt | 3 | 0x04 | Input | 94 | 2 | S32 | ENUM | 1 | 0 | - | RO | ErrStt == 0
S4 | 1 | WRITE | G1 Run/Standby | Put inverter to standby (soft stop). | RemRdy | 3 | 0x03 | Holding | 2 | 2 | S32 | ENUM | 1 | 0 | - | RW | 303 (Standby) | Recommended for standby; keep InvOpMod as-is unless full stop needed.
S4 | 2 | WRITE | G1 Run/Standby | Stop inverter (harder stop). | InvOpMod | 3 | 0x03 | Holding | 0 | 2 | S32 | ENUM | 1 | 0 | - | RW | 303 (Stop) | Optionally also RemRdy=303.
S5 | 1 | WRITE | G5 Maintenance | Commissioning/maintenance-only reset. | InstFunc | 3 | 0x03 | Holding | 30 | 2 | S32 | ENUM | 1 | 0 | - | RW | 21488 (Systemreset) | Not recommended for automatic PPC logic; gate with maintenance key.

## Interlocks_Modbus
Interlock_Group | Purpose | Channel | Unit ID | Function code | Register type | Register (DEC) | CNT (WORD) | Data type | Format | Scaling | Unit | Access | Recommended | Write Sequence / Logic
G1 Run/Standby | Primary inverter run/standby/stop control | InvOpMod | 3 | 0x03 | Holding | 0 | 2 | S32 | ENUM | 1 | - | RW | 308 (Operation) | To start: write RemRdy=308 AND InvOpMod=308. To standby: RemRdy=303. To stop: InvOpMod=303 (and optionally RemRdy=303). Must be set to Ready (308) before requesting Operation via InvOpMod.
G1 Run/Standby | Primary inverter run/standby/stop control | RemRdy | 3 | 0x03 | Holding | 2 | 2 | S32 | ENUM | 1 | - | RW | 308 (Ready) | To start: write RemRdy=308 AND InvOpMod=308. To standby: RemRdy=303. To stop: InvOpMod=303 (and optionally RemRdy=303). Must be set to Ready (308) before requesting Operation via InvOpMod.
G2 Active Power Control | Select SCADA/PPC active power control source | GriMng.WMod | 3 | 0x03 | Holding | 6 | 2 | S32 | ENUM | 1 | - | RW | 1079 (WCtlCom) | For PPC/SCADA active power limitation: set WMod=1079 (WCtlCom) THEN write WSpt (kW).
G3 Reactive/PowerFactor Control | Select SCADA/PPC reactive power or PF control source | GriMng.VArMod | 3 | 0x03 | Holding | 4 | 2 | S32 | ENUM | 1 | - | RW | 1072 (VArCtlCom) | For PPC/SCADA reactive control: set VArMod=1072 (VArCtlCom) then write VArSpt; or set VArMod=1075 (PFCtlCom) then write PFSpt; some PPC schemes use 2270 (AutoCom).
G4 Fault Handling | Fault acknowledgment actions | ErrClr | 3 | 0x03 | Holding | 8 | 2 | S32 | ENUM | 1 | - | RW | 26 (Ackn) | Write 26 once after fault cause is removed. Do not pulse continuously. Use only for safety-critical faults when allowed by site procedure. Pair with investigation of ErrNo / ProErr root cause.
G4 Fault Handling | Fault acknowledgment actions | ErrClr.ProErr | 3 | 0x03 | Holding | 20 | 2 | S32 | ENUM | 1 | - | RW | 973 (Acknowledge ProErr) | Write 26 once after fault cause is removed. Do not pulse continuously. Use only for safety-critical faults when allowed by site procedure. Pair with investigation of ErrNo / ProErr root cause.
G5 Maintenance | Commissioning / maintenance-only functions | InstFunc | 3 | 0x03 | Holding | 30 | 2 | S32 | ENUM | 1 | - | RW | 21488 (Systemreset) | Maintenance-only. Typically not exposed to operator HMI; requires explicit commissioning procedure.

## Registers_Reference
Interlock_Group | Channel | Explanation | Unit ID | Function code | Register type | Register (DEC) | CNT (WORD) | Data type | Format | Scaling | Offset | Unit | Access | SCADA_Recommended_Setting | ENUMs (value=text) | Interlock_Logic
G1 Run/Standby | InvOpMod | Operating state of the inverter, setpoint | 3 | 0x03 | Holding | 0 | 2 | S32 | ENUM | 1 | 0 | - | RW | 308 (Operation) | 303=Stop; 308=Operation | To start: write RemRdy=308 AND InvOpMod=308. To standby: RemRdy=303. To stop: InvOpMod=303 (and optionally RemRdy=303).
G1 Run/Standby | RemRdy | Put inverter into operation or standby | 3 | 0x03 | Holding | 2 | 2 | S32 | ENUM | 1 | 0 | - | RW | 308 (Ready) | 303=Standby; 308=Ready | Must be set to Ready (308) before requesting Operation via InvOpMod.
G2 Active Power Control | GriMng.WMod | Utility grid system services: Selection of procedure for setpoint for active power | 3 | 0x03 | Holding | 6 | 2 | S32 | ENUM | 1 | 0 | - | RW | 1079 (WCtlCom) | 1390=WCtlAnIn; 1079=WCtlCom; 1077=WCtlMan; 303=Off | For PPC/SCADA active power limitation: set WMod=1079 (WCtlCom) THEN write WSpt (kW).
G3 Reactive/PowerFactor Control | GriMng.VArMod | Utility grid system services: Selection of procedure for setpoint for reactive power | 3 | 0x03 | Holding | 4 | 2 | S32 | ENUM | 1 | 0 | - | RW | 1072 (VArCtlCom) | 1387=VArCtlAnIn; 1388=PFCtlAnIn; 1072=VArCtlCom; 1075=PFCtlCom; 2270=AutoCom; 1071=VArCtlMan; 1074=PFCtlMan; 303=Off | For PPC/SCADA reactive control: set VArMod=1072 (VArCtlCom) then write VArSpt; or set VArMod=1075 (PFCtlCom) then write PFSpt; some PPC schemes use 2270 (AutoCom).
G4 Fault Handling | ErrClr | Acknowledgment of the present error | 3 | 0x03 | Holding | 8 | 2 | S32 | ENUM | 1 | 0 | - | RW | 26 (Ackn) | 26=Ackn | Write 26 once after fault cause is removed. Do not pulse continuously.
G4 Fault Handling | ErrClr.ProErr | Acknowledging of safety- relevant errors | 3 | 0x03 | Holding | 20 | 2 | S32 | ENUM | 1 | 0 | - | RW | 973 (Acknowledge ProErr) | 973=--- | Use only for safety-critical faults when allowed by site procedure. Pair with investigation of ErrNo / ProErr root cause.
G5 Maintenance | InstFunc | Activation of installation functions | 3 | 0x03 | Holding | 30 | 2 | S32 | ENUM | 1 | 0 | - | RW | 21488 (Systemreset) | 21488=Systemreset | Maintenance-only. Typically not exposed to operator HMI; requires explicit commissioning procedure.
| InvMs.TotVA | Apparent power, total | 3 | 0x04 | Input | 26 | 2 | S32 | FIX0 | 1 | 0 | kVA | RO
| InvMs.TotW | Active power, total | 3 | 0x04 | Input | 28 | 2 | S32 | FIX0 | 1 | 0 | kW | RO
| InvMs.TotVAr | Reactive power, total | 3 | 0x04 | Input | 30 | 2 | S32 | FIX0 | 1 | 0 | kVAr | RO
| GriMs.Hz | Grid frequency | 3 | 0x04 | Input | 38 | 2 | S32 | FIX2 | 100 | 0 | Hz | RO
| ErrLcn | Error location of the present error | 3 | 0x04 | Input | 92 | 2 | U32 | ENUM | 1 | 0 | - | RO
| ErrStt | Error status of the inverter | 3 | 0x04 | Input | 94 | 2 | S32 | ENUM | 1 | 0 | - | RO
| ErrNo | Error number of the present error | 3 | 0x04 | Input | 96 | 2 | U32 | FIX0 | 1 | 0 | - | RO
| OpStt | Operating state of the inverter | 3 | 0x04 | Input | 98 | 2 | S32 | ENUM | 1 | 0 | - | RO
| WSpt | Active power, setpoint | 3 | 0x04 | Input | 108 | 2 | S32 | FIX0 | 1 | 0 | kW | RO
| VArSpt | Reactive power, setpoint | 3 | 0x04 | Input | 112 | 2 | S32 | FIX0 | 1 | 0 | kVAr | RO
| PFSpt | Power factor cos (phi), setpoint | 3 | 0x04 | Input | 114 | 2 | S32 | FIX4 | 10000 | 0 | - | RO
| WAval | Currently available active power | 3 | 0x04 | Input | 172 | 2 | S32 | FIX4 | 10000 | 0 | pu | RO
| VArAval | Currently available reactive power | 3 | 0x04 | Input | 174 | 2 | S32 | FIX4 | 10000 | 0 | pu | RO
| PwrOffReas | Current cause of inverter disconnection | 3 | 0x04 | Input | 178 | 2 | S32 | ENUM | 1 | 0 | - | RO

## ENUM_Key_Values
Channel | Unit_ID | Function_Code | Register_DEC | Unique_ID | ENUM_Value | ENUM_Text | Meaning / Notes | Mandatory_for_PPC_SCADA | Recommended_Value | Recommended_Text | Interlock_Group
InvOpMod | 3 | 0x03 | 0 | 329 | 303 | Stop | Command inverter to stop | YES | 308 | Operation | G1 Run/Standby
InvOpMod | 3 | 0x03 | 0 | 329 | 308 | Operation | Command inverter to operate (RUN) | YES | 308 | Operation | G1 Run/Standby
RemRdy | 3 | 0x03 | 2 | 331 | 303 | Standby | Place inverter in standby | YES | 308 | Ready | G1 Run/Standby
RemRdy | 3 | 0x03 | 2 | 331 | 308 | Ready | Allow inverter to operate | YES | 308 | Ready | G1 Run/Standby
GriMng.WMod | 3 | 0x03 | 6 | 6078 | 1390 | WCtlAnIn | Active power via analog input | YES | 1079 | WCtlCom | G2 Active Power Control
GriMng.WMod | 3 | 0x03 | 6 | 6078 | 1079 | WCtlCom | Active power via communication | YES | 1079 | WCtlCom | G2 Active Power Control
GriMng.WMod | 3 | 0x03 | 6 | 6078 | 1077 | WCtlMan | Manual active power | YES | 1079 | WCtlCom | G2 Active Power Control
GriMng.WMod | 3 | 0x03 | 6 | 6078 | 303 | Off | No active power control | YES | 1079 | WCtlCom | G2 Active Power Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1387 | VArCtlAnIn | Reactive power via analog input | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1388 | PFCtlAnIn | Power factor via analog input | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1072 | VArCtlCom | Reactive power via communication | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1075 | PFCtlCom | Power factor via communication | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 2270 | AutoCom | Automatic / PPC controlled | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1071 | VArCtlMan | Manual VAr setpoint | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1074 | PFCtlMan | Manual power factor | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 303 | Off | No reactive power control | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
ErrClr | 3 | 0x03 | 8 | 733 | 26 | Ackn | Acknowledge present error | OPTIONAL | 26 | Ackn | G4 Fault Handling
ErrClr.ProErr | 3 | 0x03 | 20 | 7211 | 973 | --- | Acknowledge safety-relevant (ProErr) errors | OPTIONAL | 973 | Acknowledge ProErr | G4 Fault Handling
InstFunc | 3 | 0x03 | 30 | 7469 | 21488 | Systemreset | System reset (ACC, DCC, RIO, Controller) | NO | 21488 | Systemreset | G5 Maintenance