## Ramping_RideThrough
Ramping parameters, ride-through states, and protection limits (Sunny Central Modbus)
Category | Unit ID | FC | Address type | Register (DEC) | CNT (words) | Channel | Data type / format | Scale | RW/RO | SCADA/PPC notes (incl. mandatory recommendations)
Ramping | 3 | 0x03 | Holding | 12 | 2 | WGraMod | S32 / ENUM | 1 | RW | Enable/Disable active power gradient. Recommended: Enable=308 for PPC/SCADA to avoid step changes.
Ramping | 3 | 0x03 | Holding | 14 | 2 | WGra | S32 / FIX3 (pu/s) | 1000 | RW | Active power gradient (rate). Define project grid-code ramp; inverter ramps internally if enabled.
Ramping | 3 | 0x03 | Holding | 16 | 2 | VArGraMod | S32 / ENUM | 1 | RW | Enable/Disable reactive power gradient. Recommended: Enable=308 to prevent fast Q steps.
Ramping | 3 | 0x03 | Holding | 18 | 2 | VArGra | S32 / FIX3 (pu/s) | 1000 | RW | Reactive power gradient (rate). Set per grid-code / PPC dynamics.
Ramping | 3 | 0x03 | Holding | 10 | 2 | VADrtPriMod | S32 / ENUM | 1 | RW | Derating priority control: VAr (16) or W (18).
Ride-through status | 3 | 0x04 | Input | 98 | 2 | OpStt | S32 / ENUM | 1 | RO | Operating state includes FRT and RampDown etc. Use for PPC/SCADA state machine.
Ride-through status | 3 | 0x04 | Input | 176 | 2 | DrtStt | S32 / ENUM | 1 | RO | Derating status includes Frt, WCtlVol, VArPrio etc. Use to diagnose P/Q limitation.
Ride-through status | 3 | 0x04 | Input | 178 | 2 | PwrOffReas | S32 / ENUM | 1 | RO | Cause of disconnection (Stop/Standby reasons). Use for alarms and restart logic.
Voltage limits | 3 | 0x03 | Holding | 40 | 2 | VCtl.Hi1Lim | S16 / FIX2 (pu) | 100 | RW | Upper switch-off limit 1 (protection setting).
Voltage limits | 3 | 0x03 | Holding | 41 | 2 | VCtl.Hi1LimTm | U32 / FIX0 (ms) | 1 | RW | Delay for VCtl.Hi1Lim trip.
Voltage limits | 3 | 0x03 | Holding | 43 | 2 | VCtl.Hi2Lim | S16 / FIX2 (pu) | 100 | RW | Upper switch-off limit 2.
Voltage limits | 3 | 0x03 | Holding | 44 | 2 | VCtl.Hi2LimTm | U32 / FIX0 (ms) | 1 | RW | Delay for VCtl.Hi2Lim trip.
Voltage limits | 3 | 0x03 | Holding | 46 | 2 | VCtl.Lo1Lim | S16 / FIX2 (pu) | 100 | RW | Lower switch-off limit 1.
Voltage limits | 3 | 0x03 | Holding | 47 | 2 | VCtl.Lo1LimTm | U32 / FIX0 (ms) | 1 | RW | Delay for VCtl.Lo1Lim trip.
Voltage limits | 3 | 0x03 | Holding | 49 | 2 | VCtl.Lo2Lim | S16 / FIX2 (pu) | 100 | RW | Lower switch-off limit 2.
Voltage limits | 3 | 0x03 | Holding | 50 | 2 | VCtl.Lo2LimTm | U32 / FIX0 (ms) | 1 | RW | Delay for VCtl.Lo2Lim trip.
Voltage limits | 3 | 0x03 | Holding | 52 | 2 | VCtl.Lo3Lim | S16 / FIX2 (pu) | 100 | RW | Lower switch-off limit 3.
Voltage limits | 3 | 0x03 | Holding | 53 | 2 | VCtl.Lo3LimTm | U32 / FIX0 (ms) | 1 | RW | Delay for VCtl.Lo3Lim trip.
Voltage limits | 3 | 0x03 | Holding | 55 | 2 | VCtl.OpMaxNom | S16 / FIX2 (pu) | 100 | RW | Upper switch-on limit (reconnect permissive).
Voltage limits | 3 | 0x03 | Holding | 56 | 2 | VCtl.OpMinNom | S16 / FIX2 (pu) | 100 | RW | Lower switch-on limit (reconnect permissive).
Frequency limits | 3 | 0x03 | Holding | 57 | 2 | HzCtl.Hi1Lim | U16 / FIX2 (Hz) | 100 | RW | Upper switch-off limit 1 (frequency protection).
Frequency limits | 3 | 0x03 | Holding | 58 | 2 | HzCtl.Hi1LimTm | U32 / FIX0 (ms) | 1 | RW | Delay for HzCtl.Hi1Lim trip.

## RideThrough_ENUMS
ENUM decoding for OpStt / DrtStt / PwrOffReas (for PPC/SCADA state machine)
Register | Channel | Value | Meaning | When relevant | SCADA/PPC action
98 | OpStt | 1787 | Init | Startup/boot | Hold commands; wait for stable state
98 | OpStt | 1394 | WaitAC | Grid check | Verify voltage/frequency within reconnect thresholds
98 | OpStt | 3524 | ConnectAC | AC closing sequence | Monitor transitions; avoid repeated commands
98 | OpStt | 1393 | WaitDC | DC check | Ensure DC available; monitor DC voltage
98 | OpStt | 3525 | ConnectDC | DC precharge/close | Wait for completion
98 | OpStt | 3526 | GridFeed | Normal operation | Enable PPC closed-loop setpoints
98 | OpStt | 3527 | FRT | Fault ride-through active | Do not issue stop unless emergency; expect Q priority/limits
98 | OpStt | 3528 | Standby | Standby mode | Return to Ready/Operation per sequence
98 | OpStt | 3530 | RampDown | Controlled reduction | Avoid conflicting setpoint steps; allow ramp logic
98 | OpStt | 1469 | ShutDown | Shutdown | Investigate PwrOffReas/ErrStt
98 | OpStt | 381 | Stop | Stopped | Restart sequence if permitted
98 | OpStt | 1392 | Error | Fault condition | Acknowledge after remedy; follow fault workflow
176 | DrtStt | 21586 | Frt | Dynamic grid support/FRT | Expect curtailment/reactive support; log event
176 | DrtStt | 21601 | WCtlVol | P limited by voltage | Review voltage profile; consider Q support strategy
176 | DrtStt | 21651 | VArPrio | P reduced due to Q priority | Normal during voltage support
176 | DrtStt | 21587 | AmpGra | Gradual increase active | Ramp active; not a fault
176 | DrtStt | 21591 | WCtlHz | Overfrequency limitation | Frequency response active
176 | DrtStt | 21590 | WCtlLoHz | Underfrequency limitation | Frequency response active
178 | PwrOffReas | 21609 | Stop: SCADA/PPC, Modbus | Stop by command | Record; restart only on request
178 | PwrOffReas | 21612 | Standby: SCADA/PPC, Modbus | Standby by command | Return to Ready/Operation
178 | PwrOffReas | 21613 | Standby: AC Synchronization | Sync issue | Verify V/f limits; retry
178 | PwrOffReas | 21615 | Standby: External Grid Error | External grid error | Clear external signal; restart
178 | PwrOffReas | 21607 | Stop: Parameter InvOpMod | InvOpMod not Operation | Set InvOpMod + RemRdy
178 | PwrOffReas | 21617 | Standby: Parameter RemRdy | RemRdy not Ready | Set RemRdy=Ready(308)

## PPC_Control_Sequence
Proposed PPC → Inverter control sequence (startup, reconnection, derating/FRT)
Phase | Step | Condition / Trigger | Readbacks to check | Writes (registers) | Write values | Interlocks / sequencing | Fail-safe / alarms
Startup | 1 | Plant enable + comms OK | ErrStt=OK; KeySw=On; OpStt != Error | GriMng.WMod; GriMng.VArMod | WCtlCom(1079); VArCtlCom(1072)/AutoCom(2270) | Set modes before setpoints | Block start if ErrStt=Error
Startup | 2 | Enable ramps (recommended) | - | WGraMod; VArGraMod | Enable(308); Enable(308) | Write together as one block if possible | If rejected, PPC must ramp externally
Startup | 3 | Set soft-start setpoints | WAval/VArAval available | WSpt; VArSpt/PFSpt | 0–5% then PPC schedule | Avoid large steps before GridFeed | Alarm if setpoint rejected
Startup | 4 | Command READY | No blocking PwrOffReas; protections OK | RemRdy | Ready(308) | Must be READY before OPERATION | Retry with backoff if standby reason persists
Startup | 5 | Command OPERATION | OpStt transitions toward GridFeed | InvOpMod | Operation (per ENUM table) | Prefer same cycle write with RemRdy | If Stop due to InvOpMod, alarm and retry
Normal | 6 | Closed-loop dispatch | OpStt=GridFeed; DrtStt expected | WSpt; VArSpt/PFSpt | Per PPC; periodic update | Keep control modes stable | If DrtStt constraints, adjust PPC outputs
Derating/FRT | 7 | Grid event (FRT/voltage/frequency) | OpStt=FRT or DrtStt includes Frt/WCtlVol/VArPrio | No writes unless mandated | Hold/limit setpoints per PPC policy | Avoid stop/standby during FRT | Log compliance event; raise alarm
Reconnection | 8 | Disturbance cleared | OpStt FRT→RampDown/Standby→Connect*→GridFeed | Maintain RemRdy/InvOpMod; keep ramps | No change unless commanded | Inverter ramps power restoration (WGra) | If repeated retries, review VCtl/HzCtl settings
Fault | 9 | ErrStt=Error or OpStt=Error | ErrNo/ErrLcn/ProErr flags | ErrClr / ErrClr.ProErr | Ackn(26) / per ProErr | Acknowledge only after root cause removed | Escalate to service if persistent

## RO_TSO_Alignment
Romanian TSO / grid-code alignment checklist (Transelectrica / ENTSO-E RfG / SR EN 50549)
Requirement area | Romania reference (document) | Typical requirement | SMA Modbus channels | SCADA evidence | Responsibility | Project action
LVRT / ride-through | Transelectrica connection technical norm for generation modules; ENTSO-E RfG framework | Stay connected per voltage-time profile; provide dynamic grid support | OpStt(FRT), DrtStt(Frt), VCtl.* limits | Trend OpStt/DrtStt; event logs + grid V/f recordings | Inverter type + settings; PPC supervision | Confirm LVRT profile & compliance tests with OR/OTS
Reactive support during faults | RfG + national implementation | Reactive current/Q support; Q priority can reduce P | VADrtPriMod, GriMng.VArMod, DrtStt(VArPrio) | Log Q response and VArPrio events | PPC + inverter controls | Define voltage support strategy & set control priority
Active power ramping/restoration | Project connection conditions + common grid code practice | Controlled ramp-up after reconnection and setpoint changes | WGraMod/WGra, DrtStt(AmpGra/WGra/WGraRecon) | Compare WSpt vs measured P; log ramp states | Inverter ramp + PPC policy | Set ramp rates per contract; verify during commissioning
Voltage/frequency protection & reconnection | Transelectrica/ANRE norms; SR EN 50549-2 for MV | Trip thresholds, delays, reconnection window | VCtl.* + HzCtl.* + OpStt states | Alarm on setting changes and trips | Commissioning settings | Lock parameters after approval; implement change control

## All_Modbus_Map
Unit ID | Function code | Register type | Register (DEC) | CNT (WORD) | Channel | Explanation | Unique ID | Data type | Format | Scaling | Offset | Unit | Access | Key for operation | SCADA notes | Section | Table | Source
2 | 0x03 | Holding | 0 | 2 |  | Version number of the SMA Modbus profile |  | U32 | RAW |  |  |  | RO | No | 32-bit value (2 registers), Big Endian word order | System parameters | Unit ID 2 | MODBUS-SCxxx-TI-en-19 §5.2
2 | 0x03 | Holding | 2 | 2 |  | Device ID of the communication interface |  | U32 | RAW |  |  |  | RO | No | 32-bit value (2 registers), Big Endian word order | System parameters | Unit ID 2 | MODBUS-SCxxx-TI-en-19 §5.2
2 | 0x03 | Holding | 6 | 2 |  | Modbus data change: Meter value is increased on each access. |  | U32 | RAW |  |  |  | RO | No | 32-bit value (2 registers), Big Endian word order | System parameters | Unit ID 2 | MODBUS-SCxxx-TI-en-19 §5.2
2 | 0x03 | Holding | 300 | 2 |  | Reading of the system time (UTC) |  | U32 | DT |  |  |  | RO | No | 32-bit value (2 registers), Big Endian word order; UTC seconds since 1970-01-01 | System parameters | Unit ID 2 | MODBUS-SCxxx-TI-en-19 §5.2
2 | 0x03 | Holding | 1104 | 2 |  | Setting of the plant time (UTC) |  | U32 | DT |  |  |  | RW | No | 32-bit value (2 registers), Big Endian word order; UTC seconds since 1970-01-01 | System parameters | Unit ID 2 | MODBUS-SCxxx-TI-en-19 §5.2
2 | 0x03 | Holding | 1106 | 2 |  | Setting of the time zone. For possible values, see Section 9.6 "Number Codes of the Time Zones", page 56. |  | U32 | ENUM |  |  |  | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | System parameters | Unit ID 2 | MODBUS-SCxxx-TI-en-19 §5.2
3 | 0x03 | Holding | 0 | 2 | InvOpMod | Operating state of the inverter, setpoint | 329 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 0 | 2 | DcMs.Vol | DC voltage DC plus to DC minus | 597 | S32 | FIX1 | 10 | 0 | V | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 2 | 2 | RemRdy | Put inverter into operation or standby | 331 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 2 | 2 | DcMs.Amp.Stk1 | DC current inverter bridge 1 | 600 | S32 | FIX0 | 1 | 0 | A | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 4 | 2 | GriMng.VArMod | Utility grid system services: Selection of procedure for setpoint for reactive power | 6080 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 4 | 2 | DcMs.Amp.Stk2 | DC current inverter bridge 2 | 601 | S32 | FIX0 | 1 | 0 | A | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 6 | 2 | GriMng.WMod | Utility grid system services: Selection of procedure for setpoint for active power | 6078 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 6 | 2 | DcMs.Amp.Stk3 | DC current inverter bridge 3 | 602 | S32 | FIX0 | 1 | 0 | A | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 8 | 2 | ErrClr | Acknowledgment of the present error | 733 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 8 | 2 | DcMs.TotAmp | DC current, total | 6146 | S32 | FIX0 | 1 | 0 | A | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 10 | 2 | VADrtPriMod* | Prioritizing of control of derating | 730 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 10 | 2 | DcMs.TotWatt | DC power, total | 603 | S32 | FIX0 | 1 | 0 | kW | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 12 | 2 | WGraMod* | Activates the active power gradient | 725 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 12 | 2 | InvMs.DclVol.Stk1 | DC voltage of the inverter bridge 1 | 616 | S32 | FIX1 | 10 | 0 | V | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 14 | 2 | WGra* | Active power gradient | 726 | S32 | FIX3 | 1000 | 0 | pu/s | RW | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/1000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 14 | 2 | InvMs.DclVol.Stk2 | DC voltage of the inverter bridge 2 | 617 | S32 | FIX1 | 10 | 0 | V | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 16 | 2 | VArGraMod* | Activates the reactive power gradient | 727 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 16 | 2 | InvMs.DclVol.Stk3 | DC voltage of the inverter bridge 3 | 618 | S32 | FIX1 | 10 | 0 | V | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 18 | 2 | VArGra* | Reactive power gradient | 728 | S32 | FIX3 | 1000 | 0 | pu/s | RW | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/1000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 18 | 2 | InvMs.TotA.PhsA | AC current L1, total | 408 | S32 | FIX0 | 1 | 0 | A | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 20 | 2 | ErrClr.ProErr | Acknowledging of safety- relevant errors | 7211 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 20 | 2 | InvMs.TotA.PhsB | AC current L2, total | 409 | S32 | FIX0 | 1 | 0 | A | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 22 | 2 | GriMng.InvVArMod* | Grid management services: specification of reactive power setpoint by the inverter | 6088 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 22 | 2 | InvMs.TotA.PhsC | AC current L3, total | 410 | S32 | FIX0 | 1 | 0 | A | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 24 | 2 | InvMs.PF | Power factor (cos phi) | 404 | S32 | FIX4 | 10000 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10000 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 26 | 2 | Bfp.Ena | Activation of the function | 7372 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 26 | 2 | InvMs.TotVA | Apparent power, total | 401 | S32 | FIX0 | 1 | 0 | kVA | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 28 | 2 | GriMng.VolNomMod | Backfeed Power Grid management services: setpoint via AC voltage | 7449 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 28 | 2 | InvMs.TotW | Active power, total | 402 | S32 | FIX0 | 1 | 0 | kW | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 30 | 2 | InstFunc | Activation of installation functions | 7469 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 30 | 2 | InvMs.TotVAr | Reactive power, total | 403 | S32 | FIX0 | 1 | 0 | kVAr | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 32 | 2 | GriMs.V.PhsAB | Line-to-line voltage L1-L2, utility grid | 405 | S32 | FIX1 | 10 | 0 | V | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 34 | 2 | PvGnd.OpnRemGfdi | Open the Remote GFDI | 7682 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 34 | 2 | GriMs.V.PhsBC | Line-to-line voltage L2-L3, utility grid | 406 | S32 | FIX1 | 10 | 0 | V | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 36 | 2 | StbySfCapacMod | Activation of standby mode of the sine-wave filter capacitor | 7913 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 36 | 2 | GriMs.V.PhsCA | Line-to-line voltage L3-L1, utility grid | 407 | S32 | FIX1 | 10 | 0 | V | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 38 | 2 | Aid.Mod* | Activation of active islanding detection | 709 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 38 | 2 | GriMs.Hz | Grid frequency | 607 | S32 | FIX2 | 100 | 0 | Hz | RO | Yes | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 40 | 2 | TmpCab.Acc | Temperature in the AC range | 751 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 42 | 2 | TmpCab.Dcc | Temperature in the DC range | 750 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 44 | 2 | TmpCab.Rio | Temperature in the electronics area | 752 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 46 | 2 | TmpCab.Max | Temperature in interior, maximum value | 6130 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 48 | 2 | TmpStk.IgbtMax | Temperature of the inverter bridge (switch), maximum value | 6100 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 50 | 2 | TmpStk.PcbMax | Temperature of the inverter bridge (assembly), maximum value | 6099 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 52 | 2 | TmpExl | Outside temperature | 759 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 54 | 2 | TmpTrf | Temperature of the MV transformer | 6107 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 56 | 2 | DcSw1Stt | Switching status of the DC load- break switch 1 | 611 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 58 | 2 | DcSw2Stt | Switching status of the DC load- break switch 2 | 721 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 60 | 2 | DcSw3Stt | Switching status of the DC load- break switch 3 | 722 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 62 | 2 | AcSwStt | Switching status of the AC circuit breaker | 6202 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 66 | 2 | CapacSwStt | Switching state of the capacitor contactor | 6708 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 68 | 2 | PrchrgSwStt | Switching status of the pre-charging contactor | 6707 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 70 | 2 | Cnt.TotFeedTm | Feed-in time | 6779 | U32 | FIX0 | 1 | 0 | s | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 71 | 1 | WGraStr* | frequency: lower switch-on limit Start-up ramp for active power | 7523 | U16 | FIX3 | 1000 | 0 | pu/s | RW | No | 16-bit value (1 register); Apply scaling: raw/1000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 72 | 2 | Cnt.TotOpTm | Operating time | 6777 | U32 | FIX0 | 1 | 0 | s | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 73 | 1 | VArCtlVol.LoVolRef3* | AC voltage-dependent reactive power control: reference point 3 (below reference point 1) | 7523 | S16 | FIX3 | 1000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/1000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x03 | Holding | 74 | 1 | VArCtlVol.LoVolRef2* | AC voltage-dependent reactive power control: reference point 2 (below reference point 1) | 6050 | S16 | FIX3 | 1000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/1000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 74 | 2 | Cnt.TotWatthIn | DC energy drawn, total | 7119 | S32 | FIX2 | 100 | 0 | MWh | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 76 | 1 | VArCtlVol.HiVolRef2* | VArCtlVol.LoVolRef1 AC voltage-dependent reactive 75 6048 S16 1000 0 FIX3 pu HiVolRef1* power control: reference point 1 AC voltage-dependent reactive power control: reference point 2 (via reference point 1) | 6052 | S16 | FIX3 | 1000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/1000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 76 | 2 | Cnt.TotWhOut | AC energy fed in, total | 7118 | S32 | FIX2 | 100 | 0 | MWh | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 77 | 1 | VArCtlVol.HiVolRef3* | AC voltage-dependent reactive power control: reference point 3 (via reference point 1) | 6053 | S16 | FIX3 | 1000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/1000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x03 | Holding | 78 | 1 | VArCtlVol.LoGra3* | AC voltage-dependent reactive power control: gradient 3 (from reference point 3) | 6058 | S16 | FIX2 | 100 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 78 | 2 | Cnt.WatthIn | DC energy drawn that day | 6771 | S32 | FIX2 | 100 | 0 | MWh | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 79 | 1 | VArCtlVol.LoGra2* | AC voltage-dependent reactive power control: gradient 2 (from reference point 2) | 6056 | S16 | FIX2 | 100 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x03 | Holding | 80 | 1 | VArCtlVol.LoGra1* | AC voltage-dependent reactive power control: gradient 1 (from reference point 1) | 6054 | S16 | FIX2 | 100 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 80 | 2 | Cnt.WhOut | AC energy fed in that day | 6767 | S32 | FIX2 | 100 | 0 | MWh | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 81 | 1 | VArCtlVol.HiGra1* | AC voltage-dependent reactive power control: gradient 1 (from reference point 1) | 6055 | S16 | FIX2 | 100 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x03 | Holding | 82 | 1 | VArCtlVol.HiGra2* | AC voltage-dependent reactive power control: gradient 2 (from reference point 2) | 6057 | S16 | FIX2 | 100 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 82 | 2 | Cnt.FanCab1Tm | Operating time of the interior fan 1 | 6793 | U32 | FIX0 | 1 | 0 | s | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 83 | 1 | VArCtlVol.HiGra3* | AC voltage-dependent reactive power control: gradient 3 (from reference point 3) | 6059 | S16 | FIX2 | 100 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x03 | Holding | 84 | 2 | WCtlHzMod | Activation of frequency- dependent active power control | 361 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 84 | 2 | Cnt.FanCab2Tm | Operating time of the interior fan 2 | 6795 | U32 | FIX0 | 1 | 0 | s | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 86 | 2 | Cnt.FanStkTm | Operating time of the inverter bridge fan | 6791 | U32 | FIX0 | 1 | 0 | s | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 88 | 2 | Cnt.HtCabTm | Operating time of the interior heater | 6797 | U32 | FIX0 | 1 | 0 | s | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 90 | 1 | WCtlHz.W2* | Frequency-dependent active U16 100 0 FIX2 Hz 86 WCtlHz.Hz1 power control: cutoff frequency 364 of the 1st radio spectrum Frequency-dependent active U16 100 0 FIX2 Hz 87 WCtlHz.Hz2 power control: cutoff frequency 365 of the 2st radio spectrum Frequency-dependent active U16 100 0 FIX2 Hz 88 WCtlHz.Hz3 power control: cutoff frequency 366 of the 2nd radio spectrum Frequency-dependent active U16 100 0 FIX2 Hz 89 WCtlHz.Hz4 power control: cutoff frequency 708 of the 4th radio spectrum Frequency-dependent active power control: power referring to the inverter at the beginning of the second area | 6584 | S16 | FIX3 | 1000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/1000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 90 | 2 | Cnt.HtLoExlTmpTm | Operating time of the -40 C interior heater | 6799 | U32 | FIX0 | 1 | 0 | s | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 91 | 1 | WCtlHz.W3* | Frequency-dependent active power control: power referring to the inverter at the beginning of the third area | 6586 | S16 | FIX3 | 1000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/1000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x03 | Holding | 92 | 1 | WCtlHz.W4* | Frequency-dependent active power control: power referring to the inverter at the beginning of the fourth area | 6588 | S16 | FIX3 | 1000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/1000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 92 | 2 | ErrLcn | Error location of the present error | 6968 | U32 | ENUM | 1 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 93 | 2 | WCtlVol.Ena* | Activation of AC voltage- dependent active power control | 8156 | S32 | ENUM | 1 | 0 | - | RW | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 94 | 2 | ErrStt | Error status of the inverter | 328 | S32 | ENUM | 1 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 95 | 1 | WCtlVol.Vol1* | AC voltage-dependent active power control: voltage at reference point 1 | 8160 | S16 | FIX4 | 10000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/10000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x03 | Holding | 96 | 1 | WCtlVol.Vol2* | AC voltage-dependent active power control: voltage at reference point 2 | 8162 | S16 | FIX4 | 10000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/10000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 96 | 2 | ErrNo | Error number of the present error | 823 | U32 | FIX0 | 1 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 97 | 1 | WCtlVol.Vol3* | AC voltage-dependent active power control: voltage at reference point 3 | 8164 | S16 | FIX4 | 10000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/10000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x03 | Holding | 98 | 1 | WCtlVol.Vol4* | AC voltage-dependent active power control: voltage at reference point 4 | 8166 | S16 | FIX4 | 10000 | 0 | pu | RW | No | 16-bit value (1 register); Apply scaling: raw/10000 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 98 | 2 | OpStt | Operating state of the inverter | 332 | S32 | ENUM | 1 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 99 | 1 | WCtlVol.W1* | AC voltage-dependent active power control: active power at reference point 1 | 8168 | S16 | FIX2 | 100 | 0 | % | RW | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x03 | Holding | 100 | 1 | WCtlVol.W2* | AC voltage-dependent active power control: active power at reference point 2 | 8170 | S16 | FIX2 | 100 | 0 | % | RW | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 100 | 2 | Rio.KeySw | Switch status of the start-stop key switch | 327 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 101 | 1 | WCtlVol.W3* | AC voltage-dependent active power control: active power at reference point 3 | 8172 | S16 | FIX2 | 100 | 0 | % | RW | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x03 | Holding | 102 | 1 | WCtlVol.W4* | AC voltage-dependent active power control: active power at reference point 4 | 8174 | S16 | FIX2 | 100 | 0 | % | RW | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1
3 | 0x04 | Input | 102 | 2 | WaitGriTm | Waiting time for grid connection | 614 | S32 | FIX1 | 10 | 0 | s | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 104 | 2 | DevInf.SerNo | Inverter serial number | 6763 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 106 | 2 | GfdiSwStt | Switching status of the GFDI | 6706 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 108 | 2 | WSpt | Active power, setpoint | 320 | S32 | FIX0 | 1 | 0 | kW | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 110 | 2 | VAMaxSpt | Maximum apparent power, setpoint | 665 | S32 | FIX1 | 10 | 0 | kVA | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 112 | 2 | VArSpt | Reactive power, setpoint | 321 | S32 | FIX0 | 1 | 0 | kVAr | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 114 | 2 | PFSpt | Power factor cos (phi), setpoint | 322 | S32 | FIX4 | 10000 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10000 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 116 | 2 | TrfPro.Pres | Fast stop hermetic protection, pressure | 7029 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 118 | 2 | TrfPro.TmpTrp | Fast stop hermetic protection, temperature | 506 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 120 | 2 | TrfPro.GasOilLev | Hermetic protection, gas fill level | 7170 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 122 | 2 | TrfPro.TmpWrn | Hermetic pressure, temperature warning | 7168 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 124 | 2 | TmpStk1.lgbt | Temperature of inverter bridge 1 (switch) | 756 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 126 | 2 | TmpStk2.lgbt | Temperature of inverter bridge 2 (switch) | 757 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 128 | 2 | TmpStk3.lgbt | Temperature of inverter bridge 3 (switch) | 758 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 130 | 2 | TmpStk1.Pcb | Maximum temperature of inverter bridge 1 (assembly) | 753 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 132 | 2 | TmpStk2.Pcb | Maximum temperature of inverter bridge 2 (assembly) | 754 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 134 | 2 | TmpStk3.Pcb | Maximum temperature of inverter bridge 3 (assembly) | 755 | S32 | FIX1 | 10 | 0 | °C | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 136 | 2 | Cnt.YstdWhOut | AC energy fed in the previous day | 7073 | S32 | FIX2 | 100 | 0 | MWh | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 138 | 2 | Cpu1UpTime | CPU running time since system start | 7225 | U32 | FIX0 | 1 | 0 | s | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 140 | 2 | PvGnd.RisIso | Insulation resistance | 6644 | S32 | FIX1 | 10 | 0 | kOhm | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 142 | 2 | PresTrf | MV transformer pressure | 7249 | S32 | FIX2 | 100 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 144 | 2 | PresTrf.ErrStt | Error status of MV transformer pressure monitoring | 7253 | S32 | ENUM | 0 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 146 | 1 | BfpBits | Status of the function Backfeed | 7383 | U16 | FIX0 | 1 | 0 | - | RO | No | 16-bit value (1 register) | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 147 | 2 | DcMs.BfpAmp | Power Backfeed Power: DC current used by customer loads | 7382 | S32 | FIX1 | 10 | 0 | A | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 149 | 2 | GriMs.Vol.PsNom | Normalized AC voltage, positive sequence | 7233 | S32 | FIX4 | 10000 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10000 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 151 | 2 | Cnt.TotDcWhOut | DC energy fed in, total | 7300 | S32 | FIX2 | 100 | 0 | MWh | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 153 | 2 | Cnt.TotAcWhIn | AC energy drawn, total | 7182 | S32 | FIX2 | 100 | 0 | MWh | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 155 | 2 | Cnt.DcWhOut | DC energy fed in that day | 7302 | S32 | FIX2 | 100 | 0 | MWh | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 157 | 2 | Cnt.AcWhIn | AC energy drawn that day | 7180 | S32 | FIX2 | 100 | 0 | MWh | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 159 | 2 | DclVolSpt | DC voltage, setpoint | 7488 | S32 | FIX1 | 10 | 0 | V | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 163 | 2 | VolNomSpt | AC voltage-dependent reactive power control: setpoint AC voltage | 7000 | S32 | FIX4 | 10000 | 0 | pu | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10000 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 167 | 1 | AuxCtl.LifeSign | Life sign with valid setpoints | 7355 | U16 | FIX0 | 1 | 0 | - | RO | No | 16-bit value (1 register) | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 168 | 2 | InvPwrVolTyp | Inverter type | 6338 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 170 | 2 | HzNomSpt | Nominal frequency for frequency- dependent control of active power | 7277 | S32 | FIX2 | 100 | 0 | Hz | RO | No | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 172 | 2 | WAval | Currently available active power | 7632 | S32 | FIX4 | 10000 | 0 | pu | RO | Yes | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10000 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 174 | 2 | VArAval | Currently available reactive power | 7633 | S32 | FIX4 | 10000 | 0 | pu | RO | Yes | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10000 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 176 | 2 | DrtStt | Current derating status | 830 | S32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 178 | 2 | PwrOffReas | Current cause of inverter disconnection | 7221 | S32 | ENUM | 1 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 180 | 2 | DiagRmgTm | Time until the next inverter self test | 7716 | U32 | FIX0 | 1 | 0 | s | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 182 | 1 | Rio.Din.FloatCtl.Wa | The float controller indicates a rn warning. | 6382 | U16 | FIX0 | 1 | 0 | - | RO | No | 16-bit value (1 register) | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 183 | 1 | Rio.Din.FloatCtl.Err | The float controller indicates a warning. | 6383 | U16 | FIX0 | 1 | 0 | - | RO | No | 16-bit value (1 register) | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 184 | 2 | WRtg | Nominal value of active power | 318 | S32 | FIX0 | 1 | 0 | kW | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 186 | 1 | Gfdi.AmpPrc | Ground current measured at the | 7986 | S16 | FIX2 | 100 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 187 | 1 | Gfdi.AmpErr | GFDI Last measured ground current in case of an error | 7988 | S16 | FIX2 | 100 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 188 | 2 | ActErrNo1 | Error number of the current error | 8045 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 190 | 2 | ActErrLcn1 | Location where the current error was detected | 8047 | U32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 192 | 2 | ActErrNo2 | Error number of the current error | 8048 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 194 | 2 | ActErrLcn2 | Location where the current error was detected | 8050 | U32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 196 | 2 | ActErrNo3 | Error number of the current error | 8051 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 198 | 2 | ActErrLcn3 | Location where the current error was detected | 8053 | U32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 200 | 2 | ActErrNo4 | Error number of the current error | 8054 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 202 | 2 | ActErrLcn4 | Location where the current error was detected | 8056 | U32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 204 | 2 | ActErrNo5 | Error number of the current error | 8057 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 206 | 2 | ActErrLcn5 | Location where the current error was detected | 8059 | U32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 208 | 2 | ActErrNo6 | Error number of the current error | 8060 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 210 | 2 | ActErrLcn6 | Location where the current error was detected | 8062 | U32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 212 | 2 | ActErrNo7 | Error number of the current error | 8063 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 214 | 2 | ActErrLcn7 | Location where the current error was detected | 8065 | U32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 216 | 2 | ActErrNo8 | Error number of the current error | 8066 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 218 | 2 | ActErrLcn8 | Location where the current error was detected | 8068 | U32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 220 | 2 | ActErrNo9 | Error number of the current error | 8069 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 222 | 2 | ActErrLcn9 | Location where the current error was detected | 8071 | U32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 224 | 2 | ActErrNo10 | Error number of the current error | 8072 | U32 | FIX0 | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 226 | 2 | ActErrLcn10 | Location where the current error was detected | 8074 | U32 | ENUM | 1 | 0 | - | RO | No | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
32/33/34 | 0x04 | Input | 11 | 1 | DcMs.AmpMsCnt | Number of available inputs |  | U16 | FIX0 | 1 | 0 | - | RO | No | 16-bit value (1 register) | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 54 | 1 | Dat.UpdCnt | Channel for monitoring of data transmission |  | U16 | FIX0 | 1 | 0 | - | RO | No | 16-bit value (1 register) | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 55 | 1 | DcMs.Amp.01 | DC current input 1 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 56 | 1 | DcMs.Amp.02 | DC current input 2 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 57 | 1 | DcMs.Amp.03 | DC current input 3 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 58 | 1 | DcMs.Amp.04 | DC current input 4 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 59 | 1 | DcMs.Amp.05 | DC current input 5 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 60 | 1 | DcMs.Amp.06 | DC current input 6 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 61 | 1 | DcMs.Amp.07 | DC current input 7 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 62 | 1 | DcMs.Amp.08 | DC current input 8 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 63 | 1 | DcMs.Amp.09 | DC current input 9 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 64 | 1 | DcMs.Amp.10 | DC current input 10 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 65 | 1 | DcMs.Amp.11 | DC current input 11 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 66 | 1 | DcMs.Amp.12 | DC current input 12 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 67 | 1 | DcMs.Amp.13 | DC current input 13 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 68 | 1 | DcMs.Amp.14 | DC current input 14 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 69 | 1 | DcMs.Amp.15 | DC current input 15 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
32/33/34 | 0x04 | Input | 70 | 1 | DcMs.Amp.16 | DC current input 16 |  | S16 | FIX1 | 10 | 0 | A | RO | No | 16-bit value (1 register); Apply scaling: raw/10 | Zone monitoring | Unit ID 32/33/34 - Zone monitoring | MODBUS-SCxxx-TI-en-19 §5.4
120-169 | 0x03 | Holding | 1 | 1 | InOut.DigOut.Stt | Actual status of digital output |  | U16 | FIX0 | 1 | 0 | - |  | No | 16-bit value (1 register) | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 11 | 1 | DcMs.AmpMsCnt | Number of available inputs |  | U16 | FIX0 | 1 | 0 | - |  | No | 16-bit value (1 register) | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 46 | 1 | InOut.DigIn.SttOvp | Status digital input overvoltage protection |  | U16 | FIX0 | 1 | 0 | - |  | No | 16-bit value (1 register) | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 47 | 1 | InOut.DigIn.SttDcSw | Status digital input DC switch |  | U16 | FIX0 | 1 | 0 | - |  | No | 16-bit value (1 register) | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 48 | 1 | InOut.DigIn.Stt | Status digital input |  | U16 | FIX0 | 1 | 0 | - |  | No | 16-bit value (1 register) | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 49 | 1 | DcMs.Vol | DC voltage input |  | S16 | FIX0 | 1 | 0 | V |  | No | 16-bit value (1 register) | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 50 | 1 | Aux1.TmpVal | External temperature 1 |  | S16 | FIX1 | 10 | 0 | °C |  | No | 16-bit value (1 register); Apply scaling: raw/10 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 51 | 1 | Aux2.TmpVal | External temperature 2 |  | S16 | FIX1 | 10 | 0 | °C |  | No | 16-bit value (1 register); Apply scaling: raw/10 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 52 | 1 | Cab.TmpVal | Internal temperature |  | S16 | FIX1 | 10 | 0 | °C |  | No | 16-bit value (1 register); Apply scaling: raw/10 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 53 | 1 | InOut.AnInA1 | Analogue current input 1 (AI1) |  | S16 | FIX2 | 100 | 0 | mA |  | No | 16-bit value (1 register); Apply scaling: raw/100 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 54 | 1 | Dat.UpdCnt | Channel for monitoring of data transmission |  | U16 | FIX0 | 1 | 0 | - |  | No | 16-bit value (1 register) | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 55 | 1 | DcMs.Amp.01 | DC current input 1 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 56 | 1 | DcMs.Amp.02 | DC current input 2 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 57 | 1 | DcMs.Amp.03 | DC current input 3 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 58 | 1 | DcMs.Amp.04 | DC current input 4 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 59 | 1 | DcMs.Amp.05 | DC current input 5 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 60 | 1 | DcMs.Amp.06 | DC current input 6 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 61 | 1 | DcMs.Amp.07 | DC current input 7 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 62 | 1 | DcMs.Amp.08 | DC current input 8 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 63 | 1 | DcMs.Amp.09 | DC current input 9 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 64 | 1 | DcMs.Amp.10 | DC current input 10 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 65 | 1 | DcMs.Amp.11 | DC current input 11 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 66 | 1 | DcMs.Amp.12 | DC current input 12 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 67 | 1 | DcMs.Amp.13 | DC current input 13 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 68 | 1 | DcMs.Amp.14 | DC current input 14 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 69 | 1 | DcMs.Amp.15 | DC current input 15 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 70 | 1 | DcMs.Amp.16 | DC current input 16 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 71 | 1 | DcMs.Amp.17 | DC current input 17 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 72 | 1 | DcMs.Amp.18 | DC current input 18 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 73 | 1 | DcMs.Amp.19 | DC current input 19 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 74 | 1 | DcMs.Amp.20 | DC current input 20 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 75 | 1 | DcMs.Amp.21 | DC current input 21 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 76 | 1 | DcMs.Amp.22 | DC current input 22 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 77 | 1 | DcMs.Amp.23 | DC current input 23 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 78 | 1 | DcMs.Amp.24 | DC current input 24 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 79 | 1 | DcMs.Amp.25 | DC current input 25 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 80 | 1 | DcMs.Amp.26 | DC current input 26 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 81 | 1 | DcMs.Amp.27 | DC current input 27 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 82 | 1 | DcMs.Amp.28 | DC current input 28 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 83 | 1 | DcMs.Amp.29 | DC current input 29 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 84 | 1 | DcMs.Amp.30 | DC current input 30 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 85 | 1 | DcMs.Amp.31 | DC current input 31 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5
120-169 | 0x04 | Input | 86 | 1 | DcMs.Amp.32 | DC current input 32 |  | S16 | FIX2 | 1000 | 0 | A |  | No | 16-bit value (1 register); Apply scaling: raw/1000 | String monitor | Unit ID 120-169 - Sunny String-Monitor | MODBUS-SCxxx-TI-en-19 §5.5

## Main_Inverter
Unit ID | Function code | Register type | Register (DEC) | CNT (WORD) | Channel | Explanation | Unique ID | Data type | Format | Scaling | Offset | Unit | Access | Key for operation | SCADA notes | Section | Table | Source | SCADA_Recommended_Setting | Interlock_Group | Interlock_Logic
3 | 0x03 | Holding | 0 | 2 | InvOpMod | Operating state of the inverter, setpoint | 329 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1 | 308 (Operation) | G1 Run/Standby | To start: write RemRdy=308 AND InvOpMod=308. To standby: RemRdy=303. To stop: InvOpMod=303 (and optionally RemRdy=303).
3 | 0x03 | Holding | 2 | 2 | RemRdy | Put inverter into operation or standby | 331 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1 | 308 (Ready) | G1 Run/Standby | Must be set to Ready (308) before requesting Operation via InvOpMod.
3 | 0x03 | Holding | 4 | 2 | GriMng.VArMod | Utility grid system services: Selection of procedure for setpoint for reactive power | 6080 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1 | 1072 (VArCtlCom) | G3 Reactive/PowerFactor Control | For PPC/SCADA reactive control: set VArMod=1072 (VArCtlCom) then write VArSpt; or set VArMod=1075 (PFCtlCom) then write PFSpt; some PPC schemes use 2270 (AutoCom).
3 | 0x03 | Holding | 6 | 2 | GriMng.WMod | Utility grid system services: Selection of procedure for setpoint for active power | 6078 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1 | 1079 (WCtlCom) | G2 Active Power Control | For PPC/SCADA active power limitation: set WMod=1079 (WCtlCom) THEN write WSpt (kW).
3 | 0x03 | Holding | 8 | 2 | ErrClr | Acknowledgment of the present error | 733 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1 | 26 (Ackn) | G4 Fault Handling | Write 26 once after fault cause is removed. Do not pulse continuously.
3 | 0x03 | Holding | 20 | 2 | ErrClr.ProErr | Acknowledging of safety- relevant errors | 7211 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1 | 973 (Acknowledge ProErr) | G4 Fault Handling | Use only for safety-critical faults when allowed by site procedure. Pair with investigation of ErrNo / ProErr root cause.
3 | 0x04 | Input | 26 | 2 | InvMs.TotVA | Apparent power, total | 401 | S32 | FIX0 | 1 | 0 | kVA | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 28 | 2 | InvMs.TotW | Active power, total | 402 | S32 | FIX0 | 1 | 0 | kW | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x03 | Holding | 30 | 2 | InstFunc | Activation of installation functions | 7469 | S32 | ENUM | 1 | 0 | - | RW | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Holding parameters | MODBUS-SCxxx-TI-en-19 §5.3.1 | 21488 (Systemreset) | G5 Maintenance | Maintenance-only. Typically not exposed to operator HMI; requires explicit commissioning procedure.
3 | 0x04 | Input | 30 | 2 | InvMs.TotVAr | Reactive power, total | 403 | S32 | FIX0 | 1 | 0 | kVAr | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 38 | 2 | GriMs.Hz | Grid frequency | 607 | S32 | FIX2 | 100 | 0 | Hz | RO | Yes | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/100 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 92 | 2 | ErrLcn | Error location of the present error | 6968 | U32 | ENUM | 1 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 94 | 2 | ErrStt | Error status of the inverter | 328 | S32 | ENUM | 1 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 96 | 2 | ErrNo | Error number of the present error | 823 | U32 | FIX0 | 1 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 98 | 2 | OpStt | Operating state of the inverter | 332 | S32 | ENUM | 1 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 108 | 2 | WSpt | Active power, setpoint | 320 | S32 | FIX0 | 1 | 0 | kW | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 112 | 2 | VArSpt | Reactive power, setpoint | 321 | S32 | FIX0 | 1 | 0 | kVAr | RO | Yes | 32-bit value (2 registers), Big Endian word order | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 114 | 2 | PFSpt | Power factor cos (phi), setpoint | 322 | S32 | FIX4 | 10000 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10000 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 172 | 2 | WAval | Currently available active power | 7632 | S32 | FIX4 | 10000 | 0 | pu | RO | Yes | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10000 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 174 | 2 | VArAval | Currently available reactive power | 7633 | S32 | FIX4 | 10000 | 0 | pu | RO | Yes | 32-bit value (2 registers), Big Endian word order; Apply scaling: raw/10000 | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2
3 | 0x04 | Input | 178 | 2 | PwrOffReas | Current cause of inverter disconnection | 7221 | S32 | ENUM | 1 | 0 | - | RO | Yes | 32-bit value (2 registers), Big Endian word order; Enumerated codes; see enum table for mapping | Inverter | Unit ID 3 - Input registers | MODBUS-SCxxx-TI-en-19 §5.3.2

## SCADA_Notes
SCADA integration notes (SMA Sunny Central Modbus)
Key Modbus details:
Unit ID addressing is used to select device ranges (e.g., 2 = system parameters, 3 = inverter, 32-34 = zone monitoring, 120-169 = String Monitor).
Holding registers are read/write via Modbus TCP using function codes 0x03 (read), 0x06 (write single), 0x10 (write multiple).
Input registers are read-only via Modbus TCP using function code 0x04.
32-bit values use 2 consecutive 16-bit registers; byte order is Big Endian (Motorola).
Apply the Scaling factor shown (raw value divided by Scaling). Offsets are added after scaling when non-zero.
Highlighted rows in Main_Inverter are the typical minimum set for start/stop, status, alarms, and setpoints/measurements.

## ENUM_Mappings
Channel | Unit_ID | Function_Code | Register_DEC | Unique_ID | ENUM_Value | ENUM_Text | Meaning / Notes | Mandatory_for_PPC_SCADA | Recommended_Value | Recommended_Text | Interlock_Group
InvOpMod | 3 | 0x03 | 0 | 329 | 303 | Stop | Command inverter to stop | YES | 308 | Operation | G1 Run/Standby
InvOpMod | 3 | 0x03 | 0 | 329 | 308 | Operation | Command inverter to operate (RUN) | YES | 308 | Operation | G1 Run/Standby
RemRdy | 3 | 0x03 | 2 | 331 | 303 | Standby | Place inverter in standby | YES | 308 | Ready | G1 Run/Standby
RemRdy | 3 | 0x03 | 2 | 331 | 308 | Ready | Allow inverter to operate | YES | 308 | Ready | G1 Run/Standby
GriMng.WMod | 3 | 0x03 | 6 | 6078 | 1390 | WCtlAnIn | Active power via analog input | YES | 1079 | WCtlCom | G2 Active Power Control
GriMng.WMod | 3 | 0x03 | 6 | 6078 | 1079 | WCtlCom | Active power via communication | YES | 1079 | WCtlCom | G2 Active Power Control
GriMng.WMod | 3 | 0x03 | 6 | 6078 | 1077 | WCtlMan | Manual active power | YES | 1079 | WCtlCom | G2 Active Power Control
GriMng.WMod | 3 | 0x03 | 6 | 6078 | 303 | Off | No active power control | YES | 1079 | WCtlCom | G2 Active Power Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1387 | VArCtlAnIn | Reactive power via analog input | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1388 | PFCtlAnIn | Power factor via analog input | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1072 | VArCtlCom | Reactive power via communication | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1075 | PFCtlCom | Power factor via communication | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 2270 | AutoCom | Automatic / PPC controlled | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1071 | VArCtlMan | Manual VAr setpoint | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 1074 | PFCtlMan | Manual power factor | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
GriMng.VArMod | 3 | 0x03 | 4 | 6080 | 303 | Off | No reactive power control | YES | 1072 | VArCtlCom | G3 Reactive/PowerFactor Control
ErrClr | 3 | 0x03 | 8 | 733 | 26 | Ackn | Acknowledge present error | OPTIONAL | 26 | Ackn | G4 Fault Handling
ErrClr.ProErr | 3 | 0x03 | 20 | 7211 | 973 | --- | Acknowledge safety-relevant (ProErr) errors | OPTIONAL | 973 | Acknowledge ProErr | G4 Fault Handling
InstFunc | 3 | 0x03 | 30 | 7469 | 21488 | Systemreset | System reset (ACC, DCC, RIO, Controller) | NO | 21488 | Systemreset | G5 Maintenance

## Interlocks
Interlock_Group | Registers (Channel @ Register) | Purpose | Write Sequence / Logic
G1 Run/Standby | InvOpMod @ 0, RemRdy @ 2 | Primary inverter run/standby/stop control | To start: write RemRdy=308 AND InvOpMod=308. To standby: RemRdy=303. To stop: InvOpMod=303 (and optionally RemRdy=303). Must be set to Ready (308) before requesting Operation via InvOpMod.
G2 Active Power Control | GriMng.WMod @ 6 | Select SCADA/PPC active power control source | For PPC/SCADA active power limitation: set WMod=1079 (WCtlCom) THEN write WSpt (kW).
G3 Reactive/PowerFactor Control | GriMng.VArMod @ 4 | Select SCADA/PPC reactive power or PF control source | For PPC/SCADA reactive control: set VArMod=1072 (VArCtlCom) then write VArSpt; or set VArMod=1075 (PFCtlCom) then write PFSpt; some PPC schemes use 2270 (AutoCom).
G4 Fault Handling | ErrClr @ 8, ErrClr.ProErr @ 20 | Fault acknowledgment actions | Write 26 once after fault cause is removed. Do not pulse continuously. Use only for safety-critical faults when allowed by site procedure. Pair with investigation of ErrNo / ProErr root cause.
G5 Maintenance | InstFunc @ 30 | Commissioning / maintenance-only functions | Maintenance-only. Typically not exposed to operator HMI; requires explicit commissioning procedure.

## CITIRI
|  | add | length
Step1 | Holdings | 0 | 104
Step2 | Inputs | 26 | 90 | 10 | 106
Step3 | Inputs | 116 | 112
116
116