## Holding Registers
Unit ID | Address | Channel Name | Description | Category | Unique ID | Data Type | Words (derived) | Scaling | Offset | Data Format | Unit | Access | Function Codes | Section | Source Page
2 | 1104 |  | Setting of the system time (UTC) | Parameter |  | U32 | 2 |  |  | DT |  | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 21
2 | 1106 |  | Setting of the time zone. For possible values, see Section 9.5 "Number Codes of the Time Zones", page 58 | Parameter |  | U32 | 2 |  |  | ENUM |  | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 21
2 | 40018 | FstStop | Disconnection of the inverter | Setpoint | - | U32 | 2 | 1 |  | ENUM | - | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 21
2 | 40022 | VArSpt | Reactive power setpoint Q, in % of the maximum reactive power (referred to VArExlSpt.RefVal; the reference value can be defined via the parameter VArExlSpt.RefMod) of the inverter. Value range: -100.00% to < 0% = underexcited; 0% = no reactive power; 0% to +100.00% = overexcited | Setpoint | - | S16 | 1 | 100 |  | FIX2 | % | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 21
2 | 40023 | WSpt | Active power setpoint P, in % of the maximum active power (referred to WExlSpt.RefVal; the reference value can be defined via the parameter WExlSpt.RefMod) of the inverter. Value range: 0% = No active power; < 0% to +100.00% = generator or discharge mode; -100.00% to < 0% = load or charge mode | Setpoint | - | S16 | 1 | 100 |  | FIX2 | % | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 21
2 | 40024 | VArModCfg.PFCtlComCfg.PF | Displacement power factor cos φ. Value range: 0.0000 to 0.9999 | Setpoint | - | U16 | 1 | 10000 |  | FIX4 | - | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 21
2 | 40025 | VArModCfg.PFCtlComCfg.PFExt | Excitation type of cos φ | Setpoint | - | U32 | 2 | 1 |  | ENUM | - | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 22
2 | 41261 | HzNomSpt | Nominal frequency for frequency-dependent control of active power / frequency setpoint | Setpoint | - | U32 | 2 | 1000 |  | FIX3 | Hz | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 22
2 | 41263 | VolNomSpt | Nominal AC voltage for voltage-dependent reactive power control / AC voltage setpoint | Setpoint | - | U16 | 1 | 10000 |  | FIX4 | p.u. | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 22
2 | 44039 | WSptMax | Higher priority limitation of the active power setpoint WSpt in % of the maximum active power of the inverter (referred to WExlSpt.RefVal; the reference value can be defined via the parameter WExlSpt.RefMod). Value range: 0% = No active power; < 0% to +100.00% = generator or discharge mode. Use via communication must be enabled by GriMng.WMaxMod. | Setpoint | - | S32 | 2 | 100 |  | FIX2 | % | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 22
2 | 44041 | WSptMin | Lower limitation of the active power setpoint WSpt in % of the maximum active power of the inverter (referred to WExlSpt.RefVal; the reference value can be defined via the parameter WExlSpt.RefMod). Value range: 0% = No active power; < 0% to +100.00% = generator or discharge mode; -100.00% to < 0% = load or charge mode. Use via communication must be enabled by GriMng.WMinMod. | Setpoint | - | S32 | 2 | 100 |  | FIX2 | % | RW | 03 / 06 / 16 | 5.2.1 System Parameters | 22
3 | 0 | InvOpMod | Operating state of the inverter, setpoint | Parameter | 329 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 2 | RemRdy | Put inverter into operation or standby | Parameter | 331 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 4 | GriMng.VArMod | Grid management service: Selection of procedure for setpoint for reactive power | Parameter | 6080 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 6 | GriMng.WMod | Utility grid system services: Selection of procedure for setpoint for active power | Parameter | 6078 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 8 | ErrClr | Acknowledgment of the present error | Parameter | 733 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 10 | VADrtPriMod* | Prioritizing of control of derating | Parameter | 730 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 12 | WGraMod* | Activates the active power gradient | Parameter | 725 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 14 | WGra* | Active power gradient | Parameter | 726 | S32 | 2 | 1000 | 0 | FIX3 | pu/s | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 16 | VArGraMod* | Activates the reactive power gradient | Parameter | 727 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 18 | VArGra* | Reactive power gradient | Parameter | 728 | S32 | 2 | 1000 | 0 | FIX3 | pu/s | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 20 | ErrClr.ProErr | Acknowledging of safety-relevant errors | Parameter | 7211 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 22 | GriMng.InvVArMod* | Grid management services: specification of reactive power setpoint by the inverter | Parameter | 6088 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 26 | Bfp.Ena | Activation of the function Backfeed Power | Parameter | 7372 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 28 | GriMng.VolNomMod | Grid management services: setpoint via AC voltage | Parameter | 7449 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 30 | InstFunc | Activation of installation functions | Parameter | 7469 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 34 | PvGnd.OpnRemGfdi | Open the Remote GFDI | Parameter | 7682 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 24
3 | 36 | StbySfCapacMod | Activation of the standby mode of the sine filter capacitor | Parameter | 7913 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 38 | Aid.Mod* | Activation of active islanding detection | Parameter | 709 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 40 | VCtl.Hi1Lim* | Monitoring the grid voltage: upper switch-off limit 1 | Parameter | 446 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 41 | VCtl.Hi1LimTm* | Monitoring the grid voltage: waiting time upper switch-off limit 1 | Parameter | 451 | U32 | 2 | 1 | 0 | FIX0 | ms | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 43 | VCtl.Hi2Lim* | Monitoring the grid voltage: upper switch-off limit 2 | Parameter | 447 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 44 | VCtl.Hi2LimTm* | Monitoring the grid voltage: waiting time upper switch-off limit 2 | Parameter | 452 | U32 | 2 | 1 | 0 | FIX0 | ms | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 46 | VCtl.Lo1Lim* | Monitoring the grid voltage: lower switch-off limit 1 | Parameter | 456 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 47 | VCtl.Lo1LimTm* | Monitoring the grid voltage: waiting time lower switch-off limit 1 | Parameter | 461 | U32 | 2 | 1 | 0 | FIX0 | ms | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 49 | VCtl.Lo2Lim* | Monitoring the grid voltage: lower switch-off limit 2 | Parameter | 457 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 50 | VCtl.Lo2LimTm* | Monitoring the grid voltage: waiting time lower switch-off limit 2 | Parameter | 462 | U32 | 2 | 1 | 0 | FIX0 | ms | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 52 | VCtl.Lo3Lim* | Monitoring the grid voltage: lower switch-off limit 3 | Parameter | 458 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 53 | VCtl.Lo3LimTm* | Monitoring the grid voltage: waiting time lower switch-off limit 3 | Parameter | 463 | U32 | 2 | 1 | 0 | FIX0 | ms | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 55 | VCtl.OpMaxNom* | Monitoring the grid voltage: upper switch-on limit | Parameter | 444 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 56 | VCtl.OpMinNom* | Monitoring the grid voltage: lower switch-on limit | Parameter | 445 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 57 | HzCtl.Hi1Lim* | Monitoring the grid frequency: upper switch-off limit 1 | Parameter | 468 | U16 | 1 | 100 | 0 | FIX2 | Hz | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 58 | HzCtl.Hi1LimTm* | Monitoring the grid frequency: waiting time upper switch-off limit 1 | Parameter | 474 | U32 | 2 | 1 | 0 | FIX0 | ms | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 60 | HzCtl.Hi2Lim* | Monitoring the grid frequency: upper switch-off limit 2 | Parameter | 469 | U16 | 1 | 100 | 0 | FIX2 | Hz | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 25
3 | 61 | HzCtl.Hi2LimTm* | Monitoring the grid frequency: waiting time upper switch-off limit 2 | Parameter | 475 | U32 | 2 | 1 | 0 | FIX0 | ms | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 63 | HzCtl.Lo1Lim* | Monitoring the grid frequency: lower switch-off limit 1 | Parameter | 480 | U16 | 1 | 100 | 0 | FIX2 | Hz | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 64 | HzCtl.Lo1LimTm* | Monitoring the grid frequency: waiting time lower switch-off limit 1 | Parameter | 486 | U32 | 2 | 1 | 0 | FIX0 | ms | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 66 | HzCtl.Lo2Lim* | Monitoring the grid frequency: lower switch-off limit 2 | Parameter | 481 | U16 | 1 | 100 | 0 | FIX2 | Hz | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 67 | HzCtl.Lo2LimTm* | Monitoring the grid frequency: waiting time lower switch-off limit 2 | Parameter | 487 | U32 | 2 | 1 | 0 | FIX0 | ms | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 69 | HzCtl.OpMaxNom* | Monitoring the grid frequency: upper switch-on limit | Parameter | 466 | U16 | 1 | 100 | 0 | FIX2 | Hz | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 70 | HzCtl.OpMinNom* | Monitoring the grid frequency: lower switch-on limit | Parameter | 467 | U16 | 1 | 1 | 0 | FIX0 | Hz | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 71 | WGraStr* | Start-up ramp for active power | Parameter | 7523 | U16 | 1 | 1000 | 0 | FIX3 | pu/s | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 73 | VArCtlVol.LoVolRef3* | AC voltage-dependent reactive power control: reference point 3 (below reference point 1) | Parameter | 7523 | S16 | 1 | 1000 | 0 | FIX3 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 74 | VArCtlVol.LoVolRef2* | AC voltage-dependent reactive power control: reference point 2 (below reference point 1) | Parameter | 6050 | S16 | 1 | 1000 | 0 | FIX3 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 75 | VArCtlVol.LoVolRef1HiVolRef1* | AC voltage-dependent reactive power control: reference point 1 | Parameter | 6048 | S16 | 1 | 1000 | 0 | FIX3 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 76 | VArCtlVol.HiVolRef2* | AC voltage-dependent reactive power control: reference point 2 (via reference point 1) | Parameter | 6052 | S16 | 1 | 1000 | 0 | FIX3 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 77 | VArCtlVol.HiVolRef3* | AC voltage-dependent reactive power control: reference point 3 (via reference point 1) | Parameter | 6053 | S16 | 1 | 1000 | 0 | FIX3 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 78 | VArCtlVol.LoGra3* | AC voltage-dependent reactive power control: gradient 3 (from reference point 3) | Parameter | 6058 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 79 | VArCtlVol.LoGra2* | AC voltage-dependent reactive power control: gradient 2 (from reference point 2) | Parameter | 6056 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 26
3 | 80 | VArCtlVol.LoGra1* | AC voltage-dependent reactive power control: gradient 1 (from reference point 1) | Parameter | 6054 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 81 | VArCtlVol.HiGra1* | AC voltage-dependent reactive power control: gradient 1 (from reference point 1) | Parameter | 6055 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 82 | VArCtlVol.HiGra2* | AC voltage-dependent reactive power control: gradient 2 (from reference point 2) | Parameter | 6057 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 83 | VArCtlVol.HiGra3* | AC voltage-dependent reactive power control: gradient 3 (from reference point 3) | Parameter | 6059 | S16 | 1 | 100 | 0 | FIX2 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 84 | WCtlHzMod | Activation of frequency- dependent active power control: To enable settings for this method via Modbus, the parameter WCtlHz.CfgMod must be set to W via the user interface. | Parameter | 361 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 86 | WCtlHz.Hz1 | Frequency-dependent active power control: cutoff frequency of the 1st frequency band | Parameter | 364 | U16 | 1 | 100 | 0 | FIX2 | Hz | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 87 | WCtlHz.Hz2 | Frequency-dependent active power control: cutoff frequency of the 2st frequency band | Parameter | 365 | U16 | 1 | 100 | 0 | FIX2 | Hz | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 88 | WCtlHz.Hz3 | Frequency-dependent active power control: cutoff frequency of the 3st frequency band | Parameter | 366 | U16 | 1 | 100 | 0 | FIX2 | Hz | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 89 | WCtlHz.Hz4 | Frequency-dependent active power control: cutoff frequency of the 4st frequency band | Parameter | 708 | U16 | 1 | 100 | 0 | FIX2 | Hz | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 90 | WCtlHz.W2* | Frequency-dependent active power control: power referring to the inverter at the beginning of the second area | Parameter | 6584 | S16 | 1 | 1000 | 0 | FIX3 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 91 | WCtlHz.W3* | Frequency-dependent active power control: power referring to the inverter at the beginning of the third area | Parameter | 6586 | S16 | 1 | 1000 | 0 | FIX3 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 27
3 | 92 | WCtlHz.W4* | Frequency-dependent active power control: power referring to the inverter at the beginning of the fourth area | Parameter | 6588 | S16 | 1 | 1000 | 0 | FIX3 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 93 | WCtlVol.Ena* | Activation of AC voltage- dependent active power control | Parameter | 8156 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 95 | WCtlVol.Vol1* | AC voltage-dependent active power control: voltage at reference point 1 | Parameter | 8160 | S16 | 1 | 10000 | 0 | FIX4 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 96 | WCtlVol.Vol2* | AC voltage-dependent active power control: voltage at reference point 2 | Parameter | 8162 | S16 | 1 | 10000 | 0 | FIX4 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 97 | WCtlVol.Vol3* | AC voltage-dependent active power control: voltage at reference point 3 | Parameter | 8164 | S16 | 1 | 10000 | 0 | FIX4 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 98 | WCtlVol.Vol4* | AC voltage-dependent active power control: voltage at reference point 4 | Parameter | 8166 | S16 | 1 | 10000 | 0 | FIX4 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 99 | WCtlVol.W1* | AC voltage-dependent active power control: active power at reference point 1 | Parameter | 8168 | S16 | 1 | 100 | 0 | FIX2 | % | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 100 | WCtlVol.W2* | AC voltage-dependent active power control: active power at reference point 2 | Parameter | 8170 | S16 | 1 | 100 | 0 | FIX2 | % | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 101 | WCtlVol.W3* | AC voltage-dependent active power control: active power at reference point 3 | Parameter | 8172 | S16 | 1 | 100 | 0 | FIX2 | % | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 102 | WCtlVol.W4* | AC voltage-dependent active power control: active power at reference point 4 | Parameter | 8174 | S16 | 1 | 100 | 0 | FIX2 | % | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 103-120 | Reserved | - | Reserved | - | - |  | - | - | - | - | - | - | 5.3.1 Inverter Parameter | 28
3 | 121 | WGraFlb | Active power gradient for the control in the event of a loss of communication | Parameter | 8568 | S32 | 2 | 1000 | 0 | FIX3 | pu/s | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 123 | VArGraFlb | Reactive power gradient for the control during a loss of communication | Parameter | 8572 | S32 | 2 | 1000 | 0 | FIX3 | pu/s | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 125 | VArCtlVol.VolPsNomHiLim | AC voltage-dependent reactive power control: upper limit for feedback voltage | Parameter | 8497 | S16 | 1 | 10000 | 0 | FIX4 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 28
3 | 126 | VArCtlVol.VolPsNomLoLim | AC voltage-dependent reactive power control: lower limit for feedback voltage | Parameter | 8499 | S16 | 1 | 10000 | 0 | FIX4 | pu | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 29
3 | 127 | ExlConn | External release for connection to the grid | Parameter | 8947 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 29
3 | 129 | GriMng.ExtdFlbErrClr | Grid management services: Extended fallback operation, acknowledging the error | Parameter | 8994 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 29
3 | 131 | PvGnd.RisIsoWarnLim | Limiting value for the warning of the insulation resistance | Parameter | 6640 | U16 | 1 | 10 | 0 | FIX1 | kohm | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 29
3 | 132 | PvGnd.RisIsoErrLim | Limiting value for the error of the insulation resistance | Parameter | 6642 | U16 | 1 | 10 | 0 | FIX1 | kohm | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 29
3 | 133-134 | Reserved | - | Reserved | - | - |  | - | - | - | - | - | - | 5.3.1 Inverter Parameter | 29
3 | 143 | PvGnd.OpnRemGfdiIsoMon | Activation of the insulation measurement with manually opened GFDI | Parameter | 9283 | S32 | 2 | 1 | 0 | ENUM | - | RW | 03 / 06 / 16 | 5.3.1 Inverter Parameter | 29

## Input Registers
Unit ID | Address | Channel Name | Description | Category | Unique ID | Data Type | Words (derived) | Scaling | Offset | Data Format | Unit | Access | Function Codes | Section | Source Page
2 | 0 |  | Version number of the SMA Modbus profile | Measured Value |  | U32 | 2 |  |  | FIX0 |  | RO | 04 | 5.2.2 System Parameters | 23
2 | 2 |  | Device ID of the communication interface | Measured Value |  | U32 | 2 |  |  | FIX0 |  | RO | 04 | 5.2.2 System Parameters | 23
2 | 6 |  | Modbus data change: Meter value is increased on each access. | Measured Value |  | U32 | 2 |  |  | FIX0 |  | RO | 04 | 5.2.2 System Parameters | 23
2 | 300 |  | Reading of the system time (UTC) | Measured Value |  | U32 | 2 |  |  | DT |  | RO | 04 | 5.2.2 System Parameters | 23
2 | 700 | Upd.PkgVer | Upd.PkgVer | Measured Value |  | U32 | 2 |  |  | VERSION |  | RO | 04 | 5.2.2 System Parameters | 23
2 | 709 | Upd.PkgVer.Dec | Upd.PkgVer.Dec | Measured Value |  | U32 | 2 |  |  | FIX0 |  | RO | 04 | 5.2.2 System Parameters | 23
3 | 0 | DcMs.Vol | DC voltage DC plus to DC minus | Measured Value | 597 | S32 | 2 | 10 | 0 | FIX1 | V | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 2 | DcMs.Amp.Stk1 | DC current inverter bridge 1 | Measured Value | 600 | S32 | 2 | 1 | 0 | FIX0 | A | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 4 | DcMs.Amp.Stk2 | DC current inverter bridge 2 | Measured Value | 601 | S32 | 2 | 1 | 0 | FIX0 | A | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 6 | DcMs.Amp.Stk3 | DC current inverter bridge 3 | Measured Value | 602 | S32 | 2 | 1 | 0 | FIX0 | A | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 8 | DcMs.TotAmp | DC current, total | Measured Value | 6146 | S32 | 2 | 1 | 0 | FIX0 | A | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 10 | DcMs.TotWatt | DC power, total | Measured Value | 603 | S32 | 2 | 1 | 0 | FIX0 | kW | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 12 | InvMs.DclVol.Stk1 | DC voltage of the inverter bridge 1 | Measured Value | 616 | S32 | 2 | 10 | 0 | FIX1 | V | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 14 | InvMs.DclVol.Stk2 | DC voltage of the inverter bridge 2 | Measured Value | 617 | S32 | 2 | 10 | 0 | FIX1 | V | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 16 | InvMs.DclVol.Stk3 | DC voltage of the inverter bridge 3 | Measured Value | 618 | S32 | 2 | 10 | 0 | FIX1 | V | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 18 | InvMs.TotA.PhsA | AC current L1, total | Measured Value | 408 | S32 | 2 | 1 | 0 | FIX0 | A | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 20 | InvMs.TotA.PhsB | AC current L2, total | Measured Value | 409 | S32 | 2 | 1 | 0 | FIX0 | A | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 22 | InvMs.TotA.PhsC | AC current L3, total | Measured Value | 410 | S32 | 2 | 1 | 0 | FIX0 | A | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 24 | InvMs.PF | Power factor (cos phi) | Measured Value | 404 | S32 | 2 | 10000 | 0 | FIX4 | - | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 26 | InvMs.TotVA | Apparent power, total | Measured Value | 401 | S32 | 2 | 1 | 0 | FIX0 | kVA | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 28 | InvMs.TotW | Active power, total | Measured Value | 402 | S32 | 2 | 1 | 0 | FIX0 | kW | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 30 | InvMs.TotVAr | Reactive power, total | Measured Value | 403 | S32 | 2 | 1 | 0 | FIX0 | kVAr | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 32 | GriMs.V.PhsAB | Line-to-line voltage L1-L2, utility grid | Measured Value | 405 | S32 | 2 | 10 | 0 | FIX1 | V | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 34 | GriMs.V.PhsBC | Line-to-line voltage L2-L3, utility grid | Measured Value | 406 | S32 | 2 | 10 | 0 | FIX1 | V | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 36 | GriMs.V.PhsCA | Line-to-line voltage L3-L1, utility grid | Measured Value | 407 | S32 | 2 | 10 | 0 | FIX1 | V | RO | 04 | 5.3.2 Inverter Parameter | 32
3 | 38 | GriMs.Hz | Grid frequency | Measured Value | 607 | S32 | 2 | 100 | 0 | FIX2 | Hz | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 40 | TmpCab.Acc | Temperature in the AC range | Measured Value | 751 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 42 | TmpCab.Dcc | Temperature in the DC range | Measured Value | 750 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 44 | TmpCab.Rio | Temperature in the electronics area | Measured Value | 752 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 46 | TmpCab.Max | Temperature in interior, maximum value | Measured Value | 6130 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 48 | TmpStk.IgbtMax | Temperature of the inverter bridge (switch), maximum value | Measured Value | 6100 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 50 | TmpStk.PcbMax | Temperature of the inverter bridge (assembly), maximum value | Measured Value | 6099 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 52 | TmpExl | External temperature | Measured Value | 759 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 54 | TmpTrf | Temperature of the MV transformer Not available for MVPS2500- S-AU / MVPS 2750-S-AU / MVPS 3000-S-AU / MVPS5000-S-AU / MVPS 5500-S-AU / MVPS 6000-S-AU | Measured Value | 6107 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 56 | DcSw1Stt | Switching status of the DC load-break switch 1 | Measured Value | 611 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 58 | DcSw2Stt | Switching status of the DC load-break switch 2 | Measured Value | 721 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 60 | DcSw3Stt | Switching status of the DC load-break switch 3 | Measured Value | 722 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 62 | AcSwStt | Switching status of the AC circuit breaker | Measured Value | 6202 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 66 | CapacSwStt | Switching state of the capacitor contactor | Measured Value | 6708 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 68 | PrchrgSwStt | Switching status of the pre- charging contactor | Measured Value | 6707 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 70 | Cnt.TotFeedTm | Feed-in time | Measured Value | 6779 | U32 | 2 | 1 | 0 | FIX0 | s | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 72 | Cnt.TotOpTm | Operating time | Measured Value | 6777 | U32 | 2 | 1 | 0 | FIX0 | s | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 74 | Cnt.TotWatthIn | DC energy drawn, total | Measured Value | 7119 | S32 | 2 | 100 | 0 | FIX2 | MWh | RO | 04 | 5.3.2 Inverter Parameter | 33
3 | 76 | Cnt.TotWhOut | AC energy fed in, total | Measured Value | 7118 | S32 | 2 | 100 | 0 | FIX2 | MWh | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 78 | Cnt.WatthIn | DC energy drawn that day | Measured Value | 6771 | S32 | 2 | 100 | 0 | FIX2 | MWh | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 80 | Cnt.WhOut | AC energy fed in that day | Measured Value | 6767 | S32 | 2 | 100 | 0 | FIX2 | MWh | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 82 | Cnt.FanCab1Tm | Operating time of the interior fan 1 | Measured Value | 6793 | U32 | 2 | 1 | 0 | FIX0 | s | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 84 | Cnt.FanCab2Tm | Operating time of the interior fan 2 | Measured Value | 6795 | U32 | 2 | 1 | 0 | FIX0 | s | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 86 | Cnt.FanStkTm | Operating time of the inverter bridge fan | Measured Value | 6791 | U32 | 2 | 1 | 0 | FIX0 | s | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 88 | Cnt.HtCabTm | Operating time of the interior heater | Measured Value | 6797 | U32 | 2 | 1 | 0 | FIX0 | s | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 90 | Cnt.HtLoExlTmpTm | Operating time of the -40°C interior heater | Measured Value | 6799 | U32 | 2 | 1 | 0 | FIX0 | ms | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 92 | ErrLcn | Error location of the present error | Measured Value | 6968 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 94 | ErrStt | Error status of the inverter | Measured Value | 328 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 96 | ErrNo | Error number of the present error | Measured Value | 823 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 98 | OpStt | Operating state of the inverter | Measured Value | 332 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 100 | Rio.KeySw | Switch status of the start-stop key switch | Measured Value | 327 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 102 | WaitGriTm | Waiting time for grid connection | Measured Value | 614 | S32 | 2 | 10 | 0 | FIX1 | s | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 104 | DevInf.SerNo | Serial number of the inverter | Measured Value | 6763 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 106 | GfdiSwStt | Switching status of the GFDI | Measured Value | 6706 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 108 | WSpt | Active power, setpoint | Measured Value | 320 | S32 | 2 | 1 | 0 | FIX0 | kW | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 110 | VAMaxSpt | Maximum apparent power, setpoint | Measured Value | 665 | S32 | 2 | 10 | 0 | FIX1 | kVA | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 112 | VArSpt | Reactive power, setpoint | Measured Value | 321 | S32 | 2 | 1 | 0 | FIX0 | kVAr | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 114 | PFSpt | Power factor cos (phi), setpoint | Measured Value | 322 | S32 | 2 | 10000 | 0 | FIX4 | - | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 116 | TrfPro.Pres | Fast stop hermetic protection, pressure | Measured Value | 7029 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 118 | TrfPro.TmpTrp | Fast stop hermetic protection, temperature | Measured Value | 506 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 34
3 | 120 | TrfPro.GasOilLe | Hermetic protection, gas fill level | Measured Value | 7170 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 122 | TrfPro.TmpWrn | Hermetic pressure, temperature warning | Measured Value | 7168 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 124 | TmpStk1.lgbt | Temperature of inverter bridge 1 (switch) | Measured Value | 756 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 126 | TmpStk2.lgbt | Temperature of inverter bridge 2 (switch) | Measured Value | 757 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 128 | TmpStk3.lgbt | Temperature of inverter bridge 3 (switch) | Measured Value | 758 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 130 | TmpStk1.Pcb | Maximum temperature of inverter bridge 1 (assembly) | Measured Value | 753 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 132 | TmpStk2.Pcb | Maximum temperature of inverter bridge 2 (assembly) | Measured Value | 754 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 134 | TmpStk3.Pcb | Maximum temperature of inverter bridge 3 (assembly) | Measured Value | 755 | S32 | 2 | 10 | 0 | FIX1 | °C | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 136 | Cnt.YstdWhOut | AC energy fed in the previous day | Measured Value | 7073 | S32 | 2 | 100 | 0 | FIX2 | MWh | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 138 | Cpu1UpTime | CPU running time since system start | Measured Value | 7225 | U32 | 2 | 1 | 0 | FIX0 | s | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 140 | PvGnd.RisIso | Insulation resistance | Measured Value | 6644 | S32 | 2 | 10 | 0 | FIX1 | kohm | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 142 | PresTrf | MV transformer pressure Not available for MVPS2500- S-AU / MVPS 2750-S-AU / MVPS 3000-S-AU / MVPS5000-S-AU / MVPS 5500-S-AU / MVPS 6000-S-AU | Measured Value | 7249 | S32 | 2 | 100 | 0 | FIX2 | - | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 144 | PresTrf.ErrStt | Error status of MV transformer pressure monitoring | Measured Value | 7253 | S32 | 2 | 0 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 146 | BfpBits | Status of the function Backfeed Power | Measured Value | 7383 | U16 | 1 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 147 | DcMs.BfpAmp | Backfeed Power: DC current used by customer loads | Measured Value | 7382 | S32 | 2 | 10 | 0 | FIX1 | A | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 149 | GriMs.Vol.PsNom | Normalized AC voltage, positive sequence | Measured Value | 7233 | S32 | 2 | 10000 | 0 | FIX4 | - | RO | 04 | 5.3.2 Inverter Parameter | 35
3 | 151 | Cnt.TotDcWhOut | DC energy fed in, total | Measured Value | 7300 | S32 | 2 | 100 | 0 | FIX2 | MWh | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 153 | Cnt.TotAcWhIn | AC energy drawn, total | Measured Value | 7182 | S32 | 2 | 100 | 0 | FIX2 | MWh | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 155 | Cnt.DcWhOut | DC energy fed in that day | Measured Value | 7302 | S32 | 2 | 100 | 0 | FIX2 | MWh | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 157 | Cnt.AcWhIn | AC energy drawn that day | Measured Value | 7180 | S32 | 2 | 100 | 0 | FIX2 | MWh | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 159 | DclVolSpt | DC voltage, setpoint | Measured Value | 7488 | S32 | 2 | 10 | 0 | FIX1 | V | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 161 | Reserved | - | Reserved | - | - |  | - | - | - | - | - | - | 5.3.2 Inverter Parameter | 36
3 | 163 | VolNomSpt | AC voltage-dependent reactive power control: setpoint AC voltage | Measured Value | 7000 | S32 | 2 | 10000 | 0 | FIX4 | pu | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 167 | AuxCtl.LifeSign | Life sign with valid setpoints | Measured Value | 7355 | U16 | 1 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 168 | InvPwrVolTyp | Inverter type | Measured Value | 6338 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 170 | HzNomSpt | Nominal frequency for frequency-dependent control of active power | Measured Value | 7277 | S32 | 2 | 100 | 0 | FIX2 | Hz | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 172 | WAval | Currently available active power | Measured Value | 7632 | S32 | 2 | 10000 | 0 | FIX4 | pu | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 174 | VArAval | Currently available reactive power | Measured Value | 7633 | S32 | 2 | 10000 | 0 | FIX4 | pu | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 176 | DrtStt | Current derating status | Measured Value | 830 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 178 | PwrOffReas | Current cause of inverter disconnection | Measured Value | 7221 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 180 | DiagRmgTm | Time until the next inverter self test | Measured Value | 7716 | U32 | 2 | 1 | 0 | FIX0 | s | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 182 | Rio.Din.FloatCtl.Warn | The float controller indicates a warning. | Measured Value | 6382 | U16 | 1 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 183 | Rio.Din.FloatCtl.Err | The float controller indicates an error | Measured Value | 6383 | U16 | 1 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 184 | WRtg | Nominal value of active power | Measured Value | 318 | S32 | 2 | 1 | 0 | FIX0 | kW | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 186 | Gfdi.AmpPrc | Ground current measured at the GFDI | Measured Value | 7986 | S16 | 1 | 100 | 0 | FIX2 | A | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 187 | Gfdi.AmpErr | Last measured ground current in case of an error | Measured Value | 7988 | S16 | 1 | 100 | 0 | FIX2 | A | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 188 | ActErrNo1 | Error number of the current error | Measured Value | 8045 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 36
3 | 190 | ActErrLcn1 | Location where the current error was detected | Measured Value | 8047 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 192 | ActErrNo2 | Error number of the current error | Measured Value | 8048 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 194 | ActErrLcn2 | Location where the current error was detected | Measured Value | 8050 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 196 | ActErrNo3 | Error number of the current error | Measured Value | 8051 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 198 | ActErrLcn3 | Location where the current error was detected | Measured Value | 8053 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 200 | ActErrNo4 | Error number of the current error | Measured Value | 8054 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 202 | ActErrLcn4 | Location where the current error was detected | Measured Value | 8056 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 204 | ActErrNo5 | Error number of the current error | Measured Value | 8057 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 206 | ActErrLcn5 | Location where the current error was detected | Measured Value | 8059 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 208 | ActErrNo6 | Error number of the current error | Measured Value | 8060 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 210 | ActErrLcn6 | Location where the current error was detected | Measured Value | 8062 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 212 | ActErrNo7 | Error number of the current error | Measured Value | 8063 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 214 | ActErrLcn7 | Location where the current error was detected | Measured Value | 8065 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 216 | ActErrNo8 | Error number of the current error | Measured Value | 8066 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 218 | ActErrLcn8 | Location where the current error was detected | Measured Value | 8068 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 220 | ActErrNo9 | Error number of the current error | Measured Value | 8069 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 222 | ActErrLcn9 | Location where the current error was detected | Measured Value | 8071 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 224 | ActErrNo10 | Error number of the current error | Measured Value | 8072 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 37
3 | 226 | ActErrLcn10 | Location where the current error was detected | Measured Value | 8074 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 227-267 | Reserved | - | Reserved | - | - |  | - | - | - | - | - | - | 5.3.2 Inverter Parameter | 38
3 | 268 | VArExlSpt.RefVal | Reference value for the external reactive power setpoint | Measured Value | 8271 | S16 | 1 | 1 | 0 | FIX0 | kvar | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 269 | WExlSpt.RefVal | Reference value for the external active power setpoint | Measured Value | 8272 | S16 | 1 | 1 | 0 | FIX0 | kW | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 270 | VARtg | Nominal value of apparent power | Measured Value | 323 | S32 | 2 | 1 | 0 | FIX0 | kVA | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 272 | InvTyp | Inverter type | Measured Value | 7359 | S32 | 2 | 1 | 0 | ENUM |  | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 274 | VArRtg | Nominal value of reactive power | Measured Value | 319 | S32 | 2 | 1 | 0 | FIX0 | kvar | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 276 | DcMs.Vol.PosGnd | DC voltage of DC+ to ground | Measured Value | 598 | S32 | 2 | 10 | 0 | FIX1 | V | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 278 | DcMs.Vol.NegGnd | DC voltage of DC- to ground | Measured Value | 599 | S32 | 2 | 10 | 0 | FIX1 | V | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 286 | GriMng.ExtdFlbStt | Grid management services: Extended fallback operation, status | Measured Value | 8993 | U32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 288 | ErrRmgTm | Remaining error waiting period | Measured Value | 7114 | U32 | 2 | 1 | 0 | FIX0 | s | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 290 | Cnt.DcSw1 | Switch cycles of the DC load- break switch 1 | Measured Value | 6803 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 292 | Cnt.DcSw2 | Switch cycles of the DC load- break switch 2 | Measured Value | 6805 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 294 | Cnt.DcSw3 | Switch cycles of the DC load- break switch 3 | Measured Value | 6807 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 296 | Cnt.AcSw | Switch cycles of the AC circuit breaker | Measured Value | 6801 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 298-329 | Reserved | - | Reserved | - | - |  | - | - | - | - | - | - | 5.3.2 Inverter Parameter | 38
3 | 330 | Cnt.DcSw1Uvr | Switch cycles of the DC load- break switch 1, undervoltage release | Measured Value | 9314 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 38
3 | 332 | Cnt.DcSw2Uvr | Switch cycles of the DC load- break switch 2, undervoltage release | Measured Value | 9316 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 39
3 | 334 | Cnt.DcSw3Uvr | Switch cycles of the DC load- break switch 3, undervoltage release | Measured Value | 9318 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 39
3 | 336 | Cnt.AcSwUvr | Switch cycles of the AC circuit breaker, undervoltage release | Measured Value | 9312 | U32 | 2 | 1 | 0 | FIX0 | - | RO | 04 | 5.3.2 Inverter Parameter | 39
3 | 338 | WSptMin | Active power, minimum setpoint | Measured Value | 8253 | S32 | 2 | 1 | 0 | FIX0 | kW | RO | 04 | 5.3.2 Inverter Parameter | 39
3 | 339 | WSptMax | Active power, maximum setpoint | Measured Value | 8537 | S32 | 2 | 1 | 0 | FIX0 | kW | RO | 04 | 5.3.2 Inverter Parameter | 39
3 | 340 | RlHmdtRio | Relative humidity in the electronics area | Measured Value | 760 | S16 | 1 | 10 | 0 | FIX1 | % | RO | 04 | 5.3.2 Inverter Parameter | 39
3 | 341 | RlHmdtAcc | Relative humidity in the AC area | Measured Value | 761 | S16 | 1 | 10 | 0 | FIX1 | % | RO | 04 | 5.3.2 Inverter Parameter | 39
3 | 342 | RlHmdtDcc | Relative humidity in the DC area | Measured Value | 762 | S16 | 1 | 10 | 0 | FIX1 | % | RO | 04 | 5.3.2 Inverter Parameter | 39
3 | 343 | DrtExlStt | Derating due to outside temperature | Measured Value | 690 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 39
3 | 345 | HmdtCtl.TmCnt | Time counter to activate/deactivate dehumidification | Measured Value | 9515 | U32 | 2 | 1 | 0 | FIX0 | s | RO | 04 | 5.3.2 Inverter Parameter | 39
3 | 347 | HmdtCtl.Stt | Status of dehumidification activation | Measured Value | 9517 | S32 | 2 | 1 | 0 | ENUM | - | RO | 04 | 5.3.2 Inverter Parameter | 39

## Zone Monitoring
Configuration | Address | Unit ID 32 - Left DC Module | Unit ID 33 - Right DC Module | Notes | Source Page
Sunny Central with DC fuse switches | 55 | X21 | X41 |  | 46
Sunny Central with DC fuse switches | 56 | X22 | X42 |  | 46
Sunny Central with DC fuse switches | 57 | X23 | X43 |  | 46
Sunny Central with DC fuse switches | 58 | X24 | X44 |  | 46
Sunny Central with DC fuse switches | 59 | X25 | X45 |  | 46
Sunny Central with DC fuse switches | 60 | X26 | X46 |  | 46
Sunny Central with DC fuse switches | 61 | X27 | X47 |  | 46
Sunny Central with DC fuse switches | 62 | X28 | X48 |  | 46
Sunny Central with DC fuse switches | 63 | X29 | X49 |  | 46
Sunny Central with DC fuse switches | 64 | X30 | X50 |  | 46
Sunny Central with DC fuse switches | 65 | X31 | X51 |  | 46
Sunny Central with DC fuse switches | 66 | X32 | X52 |  | 46
Sunny Central with DC fuse switches | 67 | X33 | X53 | * Availability depends on inverter/options; see manual page 46. | 46
Sunny Central with DC fuse switches | 68 | X34 | X54 | * Availability depends on inverter/options; see manual page 46. | 46
Sunny Central with DC fuse switches | 69 | X35 | X55 | * Availability depends on inverter/options; see manual page 46. | 46
Sunny Central with DC fuse switches | 70 | X36 | X56 | * Availability depends on inverter/options; see manual page 46. | 46
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 55 | X61 | X73 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 56 | X62 | X74 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 57 | X63 | X75 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 58 | X64 | X76 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 59 | X65 | X77 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 60 | X66 | X78 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 61 | X67 | X79 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 62 | X68 | X80 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 63 | X69 | X81 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 64 | X70 | X82 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 65 | X71 | X83 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 66 | X72 | X84 |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 67 | Not used | Not used |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 68 | Not used | Not used |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 69 | Not used | Not used |  | 47
Without DC fuse switches - two-pole fused and insulated, 24 DC inputs | 70 | Not used | Not used |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 55 | X21 | X41 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 56 | X22 | X42 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 57 | X23 | X43 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 58 | X24 | X44 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 59 | X25 | X45 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 60 | X26 | X46 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 61 | X31 | X51 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 62 | X32 | X52 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 63 | X33 | X53 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 64 | X34 | X54 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 65 | X35 | X55 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 66 | X36 | X56 |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 67 | Not used | Not used |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 68 | Not used | Not used |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 69 | Not used | Not used |  | 47
Without DC fuse switches - one-pole fused, grounded and insulated, 24 DC inputs | 70 | Not used | Not used |  | 47
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 55 | X21 | X41 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 56 | X22 | X42 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 57 | X23 | X43 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 58 | X24 | X44 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 59 | X25 | X45 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 60 | X26 | X46 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 61 | X27 | X47 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 62 | X28 | X48 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 63 | X31 | X51 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 64 | X32 | X52 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 65 | X33 | X53 | With option "28 fused inputs", these registers/input straps cannot be used for Unit IDs 32 and 33. | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 66 | X34 | X54 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 67 | X35 | X55 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 68 | X36 | X56 | With option "28 fused inputs", these registers/input straps cannot be used for Unit IDs 32 and 33. | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 69 | X37 | X57 |  | 48
Without DC fuse switches - single-pole fused, grounded and insulated, 32 DC inputs | 70 | X38 | X58 |  | 48

## Notes
SMA Sunny Central Modbus v2.0 Register Map
Source document | MODBUS-SC-TI-en-20.pdf
Manual version | 2.0
Manual status | 20.03.2026
Scope | SMA native assignment tables in Sections 5.2, 5.3 and the Zone Monitoring mapping in Section 5.4. Third-party Moxa/external-device profile tables in Section 6 are not included.
Holding Registers sheet | Includes Unit ID 2 system parameters/setpoints and Unit ID 3 inverter parameters.
Input Registers sheet | Includes Unit ID 2 system input registers and Unit ID 3 inverter measured values.
Zone Monitoring sheet | Section 5.4 is kept separate because the v2.0 manual presents DC-input address mapping for Unit IDs 32/33 without explicitly classifying that table as Holding or Input. The section title also references Unit ID 34, but the displayed mapping tables on pages 46-48 show Unit IDs 32 and 33.
Words (derived) | Derived from SMA data type definitions: U16/S16 = 1 Modbus register; U32/S32 = 2 Modbus registers.
Scaling | Values reproduce the v2.0 table. Where the PDF line-wrap visually split values such as 10000 into '1000' + '0', the full numeric value has been normalized in the worksheet without changing the manual value.
Reserved ranges | Retained exactly as ranges where shown in the manual.
SunSpec marker | Channels marked with * are identified by SMA as prepared for the SunSpec profile.
Access | Holding register rows are marked RW and input-register rows RO, consistent with Sections 3.7/3.8 and the assignment-table context.
Function codes | Holding: FC03 Read Holding Registers, FC06 Write Single Holding Register, FC16 Write Multiple Registers. Input: FC04 Read Input Registers.
Confidentiality | The supplied v2.0 SMA manual is marked 'internal use only – share under NDA and with company watermark'.